Section Cover Page

Section 03 30 10 2010-06-29 Cast-In-Place Concrete (Short Form)

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if project: .1 is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

Requirements for recycled material should still be specified even if this project is not pursuing LEED Certification.

Use this Section to specify materials, formwork, accessories, reinforcement, and finishing for small scope (e.g. less than $25,000) cast-in-place concrete work except:

.1	Concrete sidewalks, driveways, aprons, pads, curbs and gutters, specified in Section 32 13 13 - Concrete Paving, Curbs and Gutters.

.2	Concrete for street light bases, car plug-in posts, guard posts, etc., specified in Section 32 17 10 - Road and Parking Appurtenances.

This Master Specification Section contains:

.1	This Cover Sheet

.2	LEED Notes and Credits

.3	Specification Section Text:

1.	General

1.1	Related Work Specified in Other Sections

1.2	Work Installed but Supplied Under Other Sections

1.3	Reference Documents

1.4	Submittals

1.5	Quality Assurance

1.6	Delivery, Storage and Handling

2.	Products

2.1	Concrete Materials

2.2	Concrete Accessories

2.3	Reinforcing Materials

2.4	Formwork Materials

2.5	Mix

2.6	Fabrication of Concrete Reinforcement

3.	Execution

3.1	Formwork

3.2	Placing Reinforcing Steel

3.3	Placing Concrete

3.4	Finishing Formed Surfaces

3.5	Finishing Flatwork

3.6	Curing

3.7	Grout

3.8	Dampproof Membrane

3.9	Waterstops

3.10	Concrete Mix Schedule

LEED Notes:

If the project is not a designated LEED project it is still be prudent to leave in the requirements for recycled material as part of an effort towards sustainability.

LEED Credits:

.1	MR Credit 4 Recycled Content: The criteria is that the sum of post-consumer recycled content plus one-half of the pre-consumer recycled content constitutes at least 10% or 20% of the total value of the materials in the project. The LEED Reference Guide identifies “Supplementary Cementing Materials” as the recycled product where it is possible to reduce the quantity of Portland Cement. Fly ash is one of the potential ingredients.

Fly ash is a coal combustion by-product of electrical power generation.  Each tonne of fly ash cement used to replace one tonne of traditional cement ingredients saves one barrel of oil associated with the costs of mining materials.

Confirm allowable percentage of supplementary cementing materials with testing agency as the percent can vary with different mix designs and seasonal factors.

Delete LEED requirements for Credit MR 4 if this credit is not part of the points being sought.

1.	General

1.1	RELATED WORK SPECIFIED IN OTHER SECTIONS

.1	[LEED Submittal Forms	Section 01 32 16].

.2	[LEED Requirements	Section 01 35 18].

.3	[Environmental Procedures	Section 01 35 20].

.4	Waste Management and Disposal	Section 01 74 19

.5	Cast-in-place concrete piles:	Section 31 62 13.

.6	Precast concrete panels:	Section [              ].

.7	Precast concrete:	Section [              ].

.8	Concrete floor finishes:	Section 03 35 10.

.9	Concrete and reinforcing in masonry walls:	Section 04 20 00.

.10	Supply of Anchor Bolts and Plates for

Structural Steel Work:	Section [             ].

1.2	WORK INSTALLED BUT SUPPLIED UNDER OTHER SECTIONS

.1	Install following materials specified to be supplied under other Sections of these project specifications:

.1	Fabricated components, anchor bolts, bearing plates, sleeves and other inserts to be built into concrete.

1.3	REFERENCE DOCUMENTS

SPEC NOTE:  Edit this Article to include only standards required to suit the project.

.1	American Concrete Institute (ACI):

| .1 | Detailing Manual - SP-66, 1988. |
| --- | --- |

.2	American Society for Testing and Materials (ASTM):

| .1 | ASTM C109/C109M-08 | Standard Test Method for Compressive Strength of Hydraulic Cement Mortars 0Using 2-in. of 50-mm Cube Specimens). |
| --- | --- | --- |
| .2 | ASTM C295-08 | Standard Guide for Petrographic Examination of Aggregates for Concrete. |
| .3 | ASTM C330-08 | Standard Specification for Lightweight Aggregates for Structural Concrete. |
| .4 | ASTM C618-08a | Standard Specification for Coal Fly Ash and Raw or Calcined Natural Pozzolan for Use in Concrete. |

.3	Canadian General Standards Board (CGSB):

| .1 | CAN/CGSB-51.34-M86 | Vapour Barrier, Polyethylene Sheet for Use in Building Construction. |
| --- | --- | --- |

.4	Canada Green Building Council (CaGBC):

| .1 | LEED Canada 2009 Rating System | LEED Canada for New Construction and Major Renovations. LEED Canada for Core and Shell Development. Website: www.cagbc.org. |
| --- | --- | --- |

.5	Canadian Standards Association (CSA):

| .1 | CAN/CSA-A3000-08 | Cementitious Materials Compendium (Consists of A5-98, A8-98, A23.5-98, A362-98, A363-98, A456.1-98, A456.2-98, A456.3-98). |
| --- | --- | --- |
| .2 | CAN/CSA-A23.1-04 | Concrete Materials and Methods of Concrete Construction. |
| .3 | CAN/CSA-A23.2-04 | Methods of Test for Concrete. |
| .4 | CAN/CSA-A23.3-04 | Design of Concrete Structures. |
| .5 | CAN/CSA G30.5-M83 (R1991) (R1998) | Welded Steel Wire Fabric for Concrete Reinforcement. |
| .6 | CAN/CSA G30.14-M83 (R1991) (R1998) | Deformed Steel Wire for Concrete Reinforcement. |
| .7 | CAN/CSA G30.15-M83 (R1991) (R1998) | Welded Deformed Steel Wire Fabric for Concrete Reinforcement. |
| .8 | CAN/CSA G30.18-M92 (R1998) | Billet Steel Bars for Concrete Reinforcement. |
| .9 | CAN/CSA-S269.3-M92 (R2008) | Concrete Formwork. |
| .10 | CAN/CSA W186-M1990 (R1998) | Welding of Reinforcing Bars in Concrete Construction. |

.5	Concrete Reinforcing Steel Institute  (CRSI):

| .1 | Reinforcing Steel Manual of Standard Practice. |
| --- | --- |

1.4	submittals

.1	Shop Drawings:

.1	Submit Shop Drawings, including placing drawings for reinforcing steel and welded steel wire fabric in accordance with Division 01.

.2	Support and placing details of reinforcing to ACI 315 and CRSI.

.2	Test and Evaluation Reports:

.1	Concrete work will be tested to CAN/CSA A23.2, or as specified herein, by a testing firm retained by the Minister.

.2	Submit proposed mix design to testing firm.

.3	Provide casual labour to the testing firm's field personnel for the purpose of obtaining and handling sample materials.

.4	Advise testing firm in advance of concrete placement.

.5	Testing firm will do the following:

.1	Take three test cylinders from each 60 m3 of concrete, or fraction thereof, of each type of concrete placed in any one day.

.2	Take samples of concrete mix close to the point of final deposit in the form.  Contractor shall provide suitable access to the Work for obtaining samples.

.3	Moist cure and test one cylinder in 7 days and moist cure and test the remaining two cylinders in 28 days.

.4	Take one additional test cylinder when the temperature is likely to fall below 0°C within 48 hours after placing and no provisions have been made to heat the concrete to greater than 10°C.  Test cylinder to be cured on job-site under same conditions as concrete it represents and tested in 7 days.

.5	Make at least one slump test and one entrained air test for each set of test cylinders taken.

.6	Results of field tests will be reported immediately to the Contractor by the field representative of the testing firm.  These results do not imply approval or disapproval of the work, but are for the Contractor's information.  Acceptability of the work will be determined by the Minister.

.7	Results of concrete tests will be forwarded to the Minister and to the Contractor.  Included with the results will be the following information: Name of Project, Date of Sampling, Name of Supplier, Delivery Truck Number, Identification of Sampling and Testing Technician and exact location in the structure of the concrete sampled.

.8	Obtain Minister's approval of reinforcing before placement of concrete commences.

.9	Strength evaluation tests and analysis:

.1	The Minister may order an independent testing firm to obtain cores, x-rays, or similar non-destructive tests.

.2	The Minister may order a load test and/or analysis as defined by CAN/CSA A23.3,  Section 20, if the non-destructive tests are impractical or inconclusive.

.3	Reinforce by additional construction or replace as directed by the Minister at own expense, concrete judged inadequate by structural analysis or by results of load tests.

.4	Pay the cost of testing and/or analysis which is required to demonstrate the adequacy of the structure which does not meet the requirements for strength or which has been placed before formwork and reinforcing have been inspected and approved by the Minister.

.5	The Minister may order additional testing at any time even though the required tests indicate that the strength requirements have been met.  In this instance the Minister will pay for those tests that meet the specified requirements and the Contractor shall pay for those that do not.

.3	Sustainable Design Submittals:

SPEC NOTE: Delete LEED submittal item if project is not to attain LEED certification or if Credit MR 4 is not being sought.

.1	LEED Submittals: submit LEED submittal forms for Credits MR 4 in accordance with Section 01 32 16 LEED Submittal Forms and Section 01 35 18 LEED Requirements and the following:

.1	Documentation including mix design identifying percent of recycled material used in the concrete.

1.5	quality assurance

SPEC NOTE:  Include this article only when a structure includes reinforced concrete construction.

.1	Failure to comply with the requirements that control strength and durability will result in the structure being considered potentially deficient.

.2	A structure will be considered potentially deficient when:

.1	Concrete used is not as specified in Concrete Mix Schedule in this Section.

.2	Reinforcing steel size, quantity, position, quality or arrangement is not as specified or detailed.

.3	Improper curing methods or materials are used.

.4	There has been inadequate protection of concrete from extremes of temperature during early stages of hardening and strength development.

.5	There has been mechanical injury from fire, construction overload or premature removal of forms.

.6	Poor workmanship is determined.

.7	The Minister has not inspected and approved formwork and reinforcement before   concrete placement.

.8	Concrete differs from the required dimensions.

1.6	delivery, storage, and handling

.1	Waste Management and Disposal:

.1	Separate waste materials for [reuse] [and] [recycling] in accordance with Section 01 74 19 Waste Management and Disposal.

2.	Products

2.1	CONCRETE MATERIALS

.1	Portland Cement:  to CAN/CSA-A3000.

.2	Aggregates:  to CAN/CSA A23.1 and as follows:

SPEC NOTE:  Delete ironstone content limitation if not applicable.

.1	Ironstone content of aggregates in exposed interior or exterior concrete subject to intermittent or continuous wetting shall not exceed the following, when tested to ASTM C295:

.1	Coarse Aggregate:  maximum 1% by mass.

.2	Fine Aggregate Retained on 2.5 mm Sieve:  maximum 1.5% by mass.

.3	Water:  to CAN/CSA A23.1.

.4	Lightweight Aggregates For Structural Lightweight Concrete:  to ASTM C330, [     ] mm to [     ] mm aggregate size.

.5	Supplementary Cementing Materials:  to CAN/CSA-A3000.

2.2	CONCRETE ACCESSORIES

.1	Liquid Membrane Forming Curing Compound:  to CAN/CSA A23.1.

.2	Grout:  non-shrink premixed types with a minimum of [16] MPa compressive strength at 24 hours.

.3	Bonding Agent:  high polymer resin emulsion, mixed with cement mortar or grout to form a water resistant adhesive bond.

.4	PVC Waterstops:  extruded polyvinylchloride with ribbed flanges, 150 mm x 5 m unless noted otherwise.

.5	Dampproof Membrane [, Reinforced]:  [150 micrometre polyethylene film to CAN/CGSB-51.34] [two [.05] [.10] [.75] mm thick polyethylene films bonded each side of asphalt treated crepe kraft paper.]

.6	Premoulded Joint Fillers: bituminous impregnated fiberboard, 12 mm thickness x required width.

.7	Dovetail Anchor slots: minimum 0.6 mm thick galvanized steel with insulated slots.

2.3 	REINFORCING MATERIALS

.1	Reinforcing Steel:  to CAN/CSA G30.18, [grade noted on drawings] [[300] [350] [400] [500] MPa]] yield grade deformed billet steel bars except for beam stirrups and column ties use only 300 MPa yield grade or 400 MPa yield grade to CAN/CSA G30.18.

.2	Reinforcing Steel:  to CAN/CSA G30.18, 400 MPa yield grade special low alloy deformed billet steel for welding and/or bending.

.3	Welded Steel Wire Fabric:  to CAN/CSA G30.5.

.4	Chairs, Bolsters, Bar Supports, Spacers:  adequate for strength and support of reinforcing.  Non-corrosive and non-staining where specified.

2.4	FORMWORK MATERIALS

.1	Formwork:  to CAN/CSA A23.1.

.2	Form Ties:  non-corrosive and non-staining at surfaces where concrete will be exposed.

SPEC NOTE: The type of form release agent specified assumes a standard concrete finish is required.

.3	Form release agents:  Ecologo certified under the Environmental Choice Program (ECP) or, if not Ecologo certified, Contractor shall:

.1	provide a product that conforms to the requirements for concrete release agents in accordance with ECP Certification Criteria Document (CCD) 143 governing Asphalt and Concrete Release Agents, excluding the provisions under Conditions for Ecologo Use and,

.2	if requested, provide the Minister with the same rights as the ECP under CCD 143 with regard to verification for product compliance.

2.5	MIX

.1	Supply concrete mix proportioned to produce concrete specified in Concrete Mix Schedule.

.2	Requirements not specified in Schedule shall conform to CAN/CSA A23.1.

.3	Use of admixtures, other than air-entraining admixtures, are not permitted without prior approval of the Minister.

2.6	FABRICATION OF CONCRETE REINFORCEMENT

.1	Fabricate reinforcing steel in accordance with CSA A23.1-00, ACI 315 and the (RSIC) Reinforcing Steel Manual of Standard Practice.

.2	Obtain Minister’s approval for locations of reinforcing splices other than those shown on placing drawings.

.3	Upon approval of Minister, weld reinforcing steel in accordance with CSA W186.

3.	Execution

  - formwork

.1	Fabricate and erect formwork in accordance with CAN/CSA-S269.3 to produce finished concrete conforming to shape, dimensions, locations and levels indicated within tolerances required by CAN/CSA-A23.1.

.2	Formwork to remain in place until concrete has attained sufficient strength to support its own weight adequately, together with the construction loads likely to be imposed.

3.2	PLACING REINFORCING STEEL

.1	Place reinforcing steel as indicated on reviewed shop drawings and in accordance with CSA A23.1.

.2	Prior to placing concrete, obtain Ministers approval of reinforcing and placement.

.3	Ensure cover to reinforcement is maintained during concrete pour.

.4	Do not field bend or field weld reinforcement, except where authorized by the Minister.

3.3	PLACING CONCRETE

.1	Perform concrete work in accordance with CAN/CSA-A23.1.

.2	Place concrete as a continuous operation stopping only at construction joints indicated on the drawings or as follows:

.1	At center of span of suspended slabs, beams and joists;

.2	in walls and columns immediately above or below floor construction;

.3	 at center of steel beam that supports concrete slab.

.3	Construction joints at center of span of suspended slabs beams and joists shall be adequately doweled and keyed.

.4	Place floor slabs on grade as one continuous pour between construction joints indicated on drawings. Control joints for each pour shall be formed by sawing a continuous 25 mm deep slot at 6 m centers each way unless otherwise indicated on drawings. Sawing shall be done as soon as the concrete has sufficiently hardened to prevent raveling of the edges but in no case later than 24 hours after the concrete slab has been placed.

.5	Isolate slabs on grade from vertical concrete using pre-moulded joint fillers extending from bottom of slab to within 12 mm of slab surface unless otherwise indicated.

.6	Use winter concreting methods in accordance with CAN/CSA A23.1 when the mean daily temperature falls below 5°C.

3.4	FINISHING FORMED SURFACES

.1	Rough-Form Finish Concrete Surfaces not Exposed to View:  in accordance with CSA A23.1. Place concrete against forms true and plane. Cut off form ties a minimum of 10 mm below concrete surface.  Patch tie holes and defects.  Remove fins exceeding 5 mm.

.2	Smooth-Form Finish Surfaces Exposed To View:   in accordance with CSA A23.1. Patch tie holes and defects.  Remove fins.

.3	Rubbed Finish Surfaces Exposed to View:  [Smooth] [Sand] [Sack] rubbed finish in accordance with CSA A23.1.

3.5	FINISHING FLATWORK

.1	Refer to Section 03 35 10 for [coloured concrete], [hardened concrete], [concrete sealer] and [wax].

.2	Interior floor slabs to be left exposed or to receive carpet, sheet vinyl or other covering requiring a smooth surface: initial finishing operations followed by mechanical floating and steel trowelling as specified in CSA A23.1, to produce hard, smooth, dense trowelled surface free from blemishes. Finish tolerance classification: [flat] [conventional] [          ].

.3	Floor slabs to receive mortar bed for ceramic or quarry tile: screed to correct grade to provide broomed texture. Finishing tolerance classification: [conventional] [             ].

.4	Equipment pads: smooth trowelled surface.

3.6	CURING

.1	Initial Curing:  Keep concrete surface continuously moist until concrete temperature has dropped several degrees.

.2	Final Curing:  Immediately following initial curing and before the concrete has dried, cure for an additional seven days, at which time the temperature of the air in contact with the concrete is above 10°C.

.3	Acceptable Curing Methods:

.1	Ponding or continuous sprinkling.

.2	Absorptive mat or fabric kept continuously wet.

.3	Damp sand, earth, or similar moist material.

.4	Continuous steam vapour mist bath not exceeding 66°C.

.5	Curing compound.

.4	Curing compounds shall not be used on concrete surfaces to receive topping or other type of bonded finish unless approved by the Minister.

.5	Protect freshly placed and consolidated concrete against damage or defacement from adverse weather conditions.

.6	Exposed Concrete Walking Surfaces Not to Receive an Integral Hardener:  Coat with curing compound of type that provides permanent seal.

3.7	GROUT

.1	Mix to flowable consistency and apply in accordance with manufacturer's instructions.

3.8	DAMPPROOF MEMBRANE

.1	Place dampproof membrane on prepared sub-grade under slabs on grade.  Lap each sheet minimum 150 mm. [Seal laps and penetrations using materials recommended by membrane manufacturer.]

  - Control joints

.1	[Cut ] [and] [form] control joints in slabs on grade at locations indicated, in accordance with CSA A23.1.  Fill with specified joint sealant.

.2	Install premoulded joint filler in expansion joints and isolation joints full depth of slab flush with finished surface.

3.10	CONCRETE MIX SCHEDULE

SPEC NOTE:  Expand and edit Concrete Mix Schedule to suit project, incorporating any required changes in specified properties.  The information included is for example only, design to suit project. Check for compatibility of admixtures, particularly when floor hardeners are being used.

SPEC NOTE:  Do not include requirements for concrete pavement, sidewalks, curbs and gutters in this Schedule.  Specify in Division 32.

SPEC NOTE:  Specify cement Types:  20 - Moderate, 30 - High Early Strength, 40 - Low Heat of Hydration, or 50 - Sulphate Resistant, when other than Type 10 - Normal is required.

3.10	CONCRETE MIX SCHEDULE

| Component | Min. Comp. Strength @ 28 Days (MPa) | Max. Water/ Cement Ratio | Nominal Agg. Size (mm) | Slump Range* (mm) | Air Content Range (%) | Minimum Cement Content (kg/m3) | Cement Type |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Weather Exposed Concrete: Exposure Class : F-2 |  |  |  |  |  |  |
| Reinforced slabs Exterior [Reinforced] Foundation walls [Exterior] [Reinforced] Columns | [32] [25] [25] | [0.45] [0.5] [0.5] | [20-5] [20-5] [20-5] | [30-70] [30-70] [70-100] | [6-8] [4-7] [4-7] | [335] [335] [335] | 10 [ ] 10 [ ] 10 [ ] |
| [ ] | [ ] | [ ] | [ ] | [ ] | [ ] | [ ] | [ ] |
| Non-Weather Exposed Concrete: Exposure Class: N |  |  |  |  |  |  |
| Columns | [25] | [0.5] | [20-5] | [70-100] | [4-6] |  | 10 [ ] |
| Reinforced slabs, beams, and walls | [25] | [0.5] | [20-5] | [50-80] | [4-6] |  | 10 [ ] |
| Reinforced foundation walls and footings | [25] | [0.5] | [20-5] | [30-70] | [4-6] |  | 10 [50] |
| Slabs-on-grade | [25] | [0.45] | [20-5] | [25-50] |  |  | 10 [ ] |
| Topping concrete | [25] | [0.5] | [10-2.5] | [50-80] |  |  | 10 [ ] |
| [ ] | [ ] | [ ] | [ ] | [ ] | [ ] | [ ] | [ ] |

*Subject to Minister's prior written approval, maximum slump may be increased beyond specified range by the use of chemical admixtures.

# END OF SECTION