Section Cover Page

Section 08 12 13 2016-10-06 Hollow Metal Frames

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if project: .1 is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

This Master Specification Section contains:

.1	This Cover Page

.2	LEED Notes and Credits

.3	Specification Section Text:

1.	General

1.1	Related Sections

1.2	Reference Documents

1.3	Submittals

1.4	Delivery, Storage and Handling

1.5	Quality Assurance

2.	Products

2.1	Materials

2.2	Fabrication

3.	Execution

3.1	Installation

LEED Notes:

Refer to Section 01 35 18 – LEED Requirements for:

- Requirements necessary to obtain points for certification.

- Confirmation of LEED perquisites and credits affecting this Section.  Not all are mandatory for certification.

Maintain built-in sustainability regardless of LEED requirements for:

- Recycling, reuse of materials, components and assemblies.

- Diversion of construction waste from landfills.

- Use of recycled materials, local materials, rapidly renewable and durable materials.

- Maintain healthy indoor environment during constructing.

- Provide for thermal comfort, access to views and daylight for indoor spaces.

- Foster innovation into facility design and planning.

LEED Credits:

1.	Materials & Resources

-	Prereq 1 - Storage & Collection of Recyclables

-	Credit 2 - Construction Waste Management

-	Credit 4 - Recycled Content

-	Credit 5 - Regional Materials

2.	Indoor Environmental Quality

-	Prereq 1 - Minimum IAQ Performance

-	Credit 4.1 - Low-Emitting Materials: Adhesives & Sealants

-	Credit 4.2 - Low-Emitting Materials: Paints and Coating

3.	Regional Priority

-	Credit 1 – Durable Building

1.	General

1.1	RELATED SECTIONS

.1	Submittal Procedures	Section 01 33 00.

.2	[LEED Requirements	Section 01 35 18.]

.3	[Waste Management and Disposal	Section 01 74 19.]

.4	Operation and Maintenance Data and Manuals	Section 01 78 23.

.5	Building-in and grouting frames in masonry:	Section 04 20 00.

.6	Grouting frames in plastered steel stud or furred walls:	Section [             .]

.7	Perimeter sealant to frames:	Section 07 92 00.

.8	Metal doors & panels:	Section 08 13 13.

.9	Supply of door hardware templates:	Section 08 70 00.

.10	Glazing of framed lights:	Section 08 81 00.

.11	Building-in frames in drywall:	Section 09 29 00.

.12	Painting:	Section 09 91 05.

1.2	reference Documents

SPEC NOTE: Edit this article to include only standards referenced within the edited version of this Section, including LEED documentation and sustainable practices.

.1	American Society for Testing and Materials (ASTM):

| .1 | ASTM A653/A653M -09 | Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process |
| --- | --- | --- |
| .2 | ASTM B29-03 (R2009) | Refined Lead |
| .3 | ASTM B749-03 (R2009) | Lead and Lead Alloy Strip, Sheet and Plate Products |

.2	Canada Green Building Council (CaGBC):

| .1 | LEED Canada 2009 Rating System | LEED Canada for New Construction and Major Renovations. LEED Canada for Core and Shell Development. Website: www.cagbc.org |
| --- | --- | --- |

.3	Canadian General Standards Board (CGSB):

| .1 | CAN/CGSB-1.181-99 | Ready-Mixed Organic Zinc-Rich Coating |
| --- | --- | --- |
| .2 | CGSB 41-GP-19Ma -84 | Rigid Vinyl Extrusions for Windows and Doors |

.4	Canadian Standards Association (CSA):

| .1 | CAN/CSA-G40.20/G40.21-04 | General Requirements for Rolled or Welded Structural Quality Steel/Structural Quality Steel |
| --- | --- | --- |
| .2 | CAN/CSA-G164-M92 (R2003) | Hot Dip Galvanizing of Irregularly Shaped Articles |
| .3 | CSA W59-03(R2008) | Welded Steel Construction (Metal Arc Welding) |

.5	Canadian Steel Door Manufacturers' Association (CSDMA):

| .1 | CSDMA, Recommended Specifications for Commercial Steel Doors and Frames, 2000 |
| --- | --- |
| .2 | CSDMA, Selection and Usage Guide for Commercial Steel Doors, 1990 |

.6	Green Seal: Standards:

| .1 | GC-03 | Green Seal Environmental Criteria for Anti-Corrosive Paints, Second Edition, January 7, 1997 |
| --- | --- | --- |
| .2 | GS-11 | Green Seal Environmental Criteria for Paint, First Edition, May 1993 |

.7	Master Painters Institute:

| .1 | Master Painters Institute Green Performance Standard GPS-1-08 |
| --- | --- |

.8	National Fire Protection Association (NFPA):

| .1 | NFPA 80-99 | Fire Doors and Fire Windows |
| --- | --- | --- |
| .2 | NFPA 252-03 | Fire Tests of Door Assemblies |

.9	South Coast Air Quality Management District (SCAQMD), California State:

| .1 | SCAQMD Rule 1168 | June 2006, Adhesives and Sealants Applications |
| --- | --- | --- |

.10	Underwriters' Laboratories of Canada (ULC):

| .1 | CAN/ULC-S701-05 | Standard for Thermal Insulation, Polystyrene, Boards and Pipe Covering |
| --- | --- | --- |
| .2 | CAN/ULC-S702-09 | Thermal Insulation, Mineral Fibre, for Buildings |
| .3 | CAN/ULC-S704-03 | Thermal Insulation, Polyurethane and Polyisocyanurate Boards, Faced |
| .4 | CAN4-S104-M80 (R1985) | Fire Tests of Door Assemblies |
| .5 | CAN4-S105-09 | Fire Door Frames Meeting the Performance Required by CAN4-S104 |

1.3	SUBMITTALS

.1	Product Data:

.1	Submit manufacturer's printed product literature, specifications and data sheet in accordance with Section 01 33 00 - Submittal Procedures.

.2	Submit [two] [        ] copies of WHMIS MSDS   Material Safety Data Sheets in accordance with Section 01 33 00 - Submittal Procedures. Indicate VOC's for adhesives.

.2	Shop Drawings:

.1	Submit shop drawings in accordance with Division 01.

.2	Clearly indicate each type of frame, material, material thicknesses, mortises, reinforcements, anchors, finish, and special features.

.3	Reference frames to door schedule.  Indicate door numbers and construction where applicable.

.3	Samples:

.1	Submit one 300 mm x 300 mm "L" section of frame showing corner detail and reinforcement for butts, [and glazing stops].

.2	Submit a 300 mm long section of removable mullion and connection parts.

SPEC NOTE:  Use these clauses above only for large projects.

.4	Sustainable Design Submittals:

SPEC NOTE: Delete LEED submittal item if project is not to attain LEED certification or if Credit MR 4 is not being sought.

.1	LEED Submittals: submit LEED submittal forms for Credit MR 4 in accordance with Section 01 32 16 LEED Submittal Forms and Section 01 35 18 LEED Requirements and the following:

.1	Recycled Content:  provide listing of products incorporating recycled content.  Include details of percentages of post-consumer and pre-consumer recycled content for materials and products.  Indicate material and product costs.

SPEC NOTE: Delete LEED submittal item if project is not to attain LEED certification or if Credit MR 5 is not being sought.

.2	LEED Submittals: submit LEED submittal forms for Credit MR 5 in accordance with Section 01 32 16 LEED Submittal Forms and Section 01 35 18 LEED Requirements and the following:

.1	Regional Materials: provide evidence that project incorporates required percentage [20] [30] % of regional materials/products, showing their cost, distances from extraction to manufacture and manufacture to project site, and total cost of materials for project.

SPEC NOTE: Delete LEED submittal item if project is not to attain LEED certification.

.3	Submit product data for site applied touch-up primer for interior applications verifying compliance with GC-03, Green Seal Environmental Criteria for Anti-Corrosive Paints, for VOC content.

SPEC NOTE: Delete the MPI Green Performance Standard if sustainable building practices are not being followed.

.4	Submit shop paint primer manufacturer's product data [verifying compliance with MPI Green Performance Standard GPS-1-08, for VOC content].

1.4	DELIVERY, Storage, and handling

.1	Delivery and Acceptance Requirements:

.1	Receive and store materials as recommended by materials manufacturer.

.2	Storage and Handling Requirements:

.1	Adequately protect surfaces from damage during moving, handling and storage.

.3	Waste Management and Disposal:

.1	Separate waste materials for [reuse] [and] [recycling] in accordance with Section 01 74 19 - Management and Disposal.

SPEC NOTE: Include clause below only if project has fire doors and frames.

1.5	QUALITY ASSURANCE

.1	Manufacture fire door and frame components and assemblies to ULC/ULI/Warnock Hersey/Factory Mutual requirements

.2	Testing Agencies: Provide doors produced under label service program of a testing agency acceptable to Authorities Having Jurisdiction, and as follows:

.1	Steel Fire Rated Doors and Frames: Labelled and listed by organization accredited by Standards Council of Canada for ratings specified or indicated.

.2	Provide fire labelled frame products for those openings requiring fire protection ratings, as scheduled:

.1	List by nationally recognized agency having factory inspection service and construct as detailed in Follow-up Service Procedures/Factory Inspection Manuals issued by agency to individual manufacturers.

.2	Fabricate rated doors, frames, and screens to labelling authority standard.

.3	Affix appropriate label to each opening requiring indicating a labelling requirement and as follows:

.1	At standard size openings: fire endurance rating [; radiation protection].

.2	At oversized openings: unclassified as to fire rating [; radiation protection].

2.	Products

2.1	MATERIALS

.1	Frames:  1.6 mm for interior locations, 1.6 mm for exterior doors, commercial quality steel cold rolled to ASTM A653M-96; zinc coated to Z275 coating designation for exterior frames, ZF075 for interior frames;

SPEC NOTE:  Specify 2.0 mm for frames with opening width in excess of 1200 mm.  Note Underwriters thickness requirements for labelled frames.

SPEC NOTE:  Use the following subparagraph for LEED projects, if recycled content materials are required for LEED Credit MRc.

SPEC NOTE:  Utilize below paragraph for LEED projects seeking MR credit 4, for materials with recycle content, post-consumer and pre-consumer.   Recycle content materials are as defined in accordance with  the Federal Trade Commission document, Guides for the Use of Environmental Marketing Claims 16 CFR.7(e).

.1	Credit MR 4 – Recycle Content [10] [20]% (Post-Consumer + ½ Pre-Consumer.

.1	Recycled Content: [         ] % post-consumer content, [        ] % pre-consumer content.

SPEC NOTE:  Use the paragraph below for LEED projects pursuing EQ credit 4.2.  Paints and coatings used on interior of the buildings (defined as inside of the weatherproofing system and applied on site) shall comply with

.1	Indoor Environmental Quality, Credit 4.2 - Low-Emitting Materials: Paints and Coating

.2	SCAQMD Rule 1113 – Architectural Coatings

.3	Maximum VOC limit  [250] [___] g/l.

.2	Accessories:  [Glazing stops], floor anchors, channel spreaders, 1.6 mm tee anchors, 1.2 mm wall stud anchors, zinc coated to ASTM A653M, coating designation ZF075 [Corrugate tee anchors for masonry bond] [Drill stud anchors for wire tie to studs] [Lag bolts, shields and bushing for existing or concrete openings].

.3	Guard Boxes:  0.50 mm steel, ZF075 coating designation zinc finish to ASTM A653M.

.4	Door Bumpers:  black neoprene.

.5	Reinforcement for Hardware:  carbon steel, prime painted, to the following thicknesses:

Hinge & Pivot reinforcements	30 mm x 250 mm  3.5 mm

Strike reinforcements	1.6 mm

Flush Bolt reinforcements	1.6 mm

Closer reinforcements	2.5 mm

Surface hardware reinforcements	2.5 mm

.6	Door Jamb Reinforcement:  100 mm x 40 mm structural steel channel to CAN3-G40.21.

2.2	FABRICATION

.1	Fabricate frames in accordance with details and approved shop drawings.  [Provide 100 mm head section where detailed.] [To Underwriters requirements and provide Underwriters labels].

.2	Mortise, reinforce, drill and tap frames and reinforcements to receive hardware using templates provided.  Locate mortising to National Builders Hardware Association Standards.

.3	Install 2 double stud bumpers on strike jamb of frame for each single door and 2 bumpers at head of double door frames.

.4	Protect strike, hinge [and overhead concealed door closer] reinforcement completely by guard boxes welded to frame.

.5	[Attach temporary wood] [Weld in 50 mm channel] spreaders to frame; ensure proper frame alignment.

.6	Where frames terminate at finished floor, provide floor plates for anchorage to floor structure.

.7	Cut mitres accurately and [weld] [secure bent tabs] on inside of frame profile.

.8	Grind welded corners to a flat plane, fill with metallic paste filler and sand to a uniform smooth finish.

.9	Fill surface depressions and butted joints with metallic paste filler and sand to a uniform smooth finish.

.10	Touch-up frames by priming areas where galvanizing is damaged.

.11	Reinforce head of frames wider than 1200 mm with 2.5 mm formed steel channel welded in place, flush with top of frame.

.12	Provide three jamb anchors per jamb for frames up to 2130 mm high and one additional for each 600 mm over 2130 mm high.

SPEC NOTE:  Ensure correct anchor type is specified for labelled frames.

.13	Minimum depth of stop:  15 mm.  [Glazing stops] [butt] [miter] joints, channel shape 15 mm wide with counter screws.

SPEC NOTE:  Use below only when hospital stop is required.

.14	Cut-off hospital stops at 45 deg. to height same as adjacent base finish; weld, fill, grind smooth and apply primer finish.

.15	Reinforce head section at junction with removable mullion.

.16	Reinforce both jambs where door openings occur in screens.  Install reinforcing continuous structure to structure.

3.	Execution

3.1	INSTALLATION

.1	Set frames in plumb and square at correct elevation.  Limit of acceptable frame distortion - 2 mm out of plumb measured on face of frame, maximum twist corner to corner of 3 mm.

.2	Secure anchorages and connections to adjacent construction.  [Anchor door jamb reinforcement securely to structure.]

.3	Brace frames solidly to maintain in position while being built-in.  [Erect knocked down frames in accordance with fabricator’s instructions.]

.4	Install a temporary horizontal wood spreader at mid-height of door opening to maintain frame width until building work completed.

.5	For frames over 1200 mm in width, provide vertical support at the centre of head.

.6	Remove temporary spreaders only after completion of adjacent work.

.7	Co-ordinate grouting of all frames solid to adjacent construction.

.8	Provide formed metal drip section full width of frame opening for exterior doors.

END OF SECTION