Section Cover Page

Section 13283 2007-03-26 Asbestos Removal

Use this Section to specify removal of materials containing asbestos, as listed below.  Always use in conjunction with Section 13281 - Asbestos Control General Requirements.  Use with Section 13282  - Asbestos Containment Procedures if full containment procedures are required.

Edit, remove from or add to this Section only in consultation with Alberta Infrastructure and Transportation specialists in asbestos control procedures.

This Section does not include requirements for dry removal of asbestos materials.  Special approval is required from Alberta Employment, Immigration and Industry, Occupational Health and Safety, before dry removal of asbestos is permitted.  Dry removal should only be considered in areas where wet removal methods would cause severe damage or where electrical systems are present which cannot be isolated as specified during the asbestos removal work.

This Master Specification Section contains:

.1	This Cover Page

.2	Specification Section Text:

1.	General

1.1	Intent

1.2	Related Sections

2.	Products

2.1	Materials

2.2	Equipment

3.	Execution

3.1	Removal, Generally

3.2	Removal of Spray Applied Asbestos

3.3	Removal of Ceiling Texture

3.4	Removal of Ceiling Tiles

3.5	Removal of Vinyl Asbestos Tile Flooring

3.6	Removal of Vinyl Asbestos Sheet Flooring

3.7	Glovebag Removal of Pipe Insulation

3.8	Cut and Wrap Removal of Insulated Pipe Fittings

3.9	Removal of Pipe and Equipment Insulation – Using Full Containment Procedures

3.10	Removal of Base Sheet From Asphalt Shingle Roofs

3.11	Asbestos Removal Schedule

1.	General

1.1	INTENT

.1	Read this Section in conjunction with Section 13281 - Asbestos Control General Requirements.

1.2	RELATED SECTIONS

.1	Asbestos Containment Procedures:	Section 13282.

.2	Asbestos Encapsulation:	Section 13284.

2.	Products

2.1	MATERIALS

.1	Amended Water:  water containing a surfactant to reduce water surface tension.  Surfactant added at a concentration to provide penetration and wetting of asbestos fibres.  Use the following:

.1	50% polyoxyethylene ester and 50% polyoxyethylene ether.

.2	Other products acceptable to the Minister.

2.2	EQUIPMENT

.1	Glovebags, Zippered:  prefabricated PVC bag, gloves and elasticized valve port, minimum 250 micrometre thickness, and with reversible double-pull, double-throw top zipper with protective flap of 250 micrometer thick PVC.

SPEC NOTE:  Include following clause when Contractor will be given the option of both types.

.2	Glovebags, Non-zippered:  prefabricated PVC bag, gloves and elasticized valve port, minimum 150 micrometre thickness, and with protective flap of 150 micrometer thick PVC.

SPEC NOTE:  Verify that location and extent of material to be removed is clearly indicated on schedule, drawings or a combination of both.

3.	Execution

3.1	REMOVAL, GENERALLY

.1	Remove saturated asbestos materials in a systematic manner.  Do not use aggregate blasting or other abrasive removal methods.

.2	Keep contaminated debris, created by removal operation, damp to prevent asbestos fibres from becoming airborne.  If contaminated debris dries out, re-soak before continuing with removal operation.

.3	Collect contaminants upon removal and put into asbestos disposal containers.  Do not permit asbestos waste to accumulate.

.4	Ensure contaminants are  completely removed from substrates and that asbestos debris is removed from pipes, ducts, fixtures and other items which may have collected contaminated debris during removal operations.

.5	Prior to sealing, purge work area air with fine spray of amended water solution.

.6	Spray exposed surfaces with Type 2 - surface film forming asbestos sealer after removal is complete and all visible asbestos is removed, in order to seal any remaining invisible asbestos fibres to the surface.  Ensure that surfaces are dry prior to spraying.

SPEC NOTE:  Delete any of the following articles that are not applicable.  Consult with Alberta Infrastructure and Transportation specialist before specifying a removal procedure required, but not included among the following.

3.2	REMOVAL OF SPRAY APPLIED ASBESTOS

.1	Remove spray applied asbestos under full containment conditions in accordance with Section 13282.

.2	Pierce covering material such as paint or sealant to permit saturation of contaminant and contaminated material with amended water.

.3	Immediately prior to commencing removal, spray contaminant and contaminated material with amended water until saturated, using an airless spray applicator.

3.3	REMOVAL OF CEILING TEXTURE

.1	Use full containment procedures in accordance with Section 13282, Containment Procedures.

.2	Completely remove contaminated ceiling texture, including over-spray in concealed spaces above ceilings.

.3	Saturate contaminants and contaminated materials with amended water immediately before removal.

.4	Where contaminated texture is covered with a coating and where practicable, pierce coating to permit saturation of contaminant with amended water.  Where saturation is not possible, provide a continuous misting of amended water on affected areas during removal.

3.4	REMOVAL OF CEILING TILES

SPEC NOTE:  Consult Alberta Infrastructure and Transportation specialist in hazardous materials for conditions under which full containment may not be necessary.

.1	Remove existing contaminated ceiling tile under full containment conditions in accordance with Section 13282.

.2	Lightly mist tile surfaces with amended water to contain fibres during removal.  Do not saturate tiles.

.3	Cut tiles within containment area.  Use wet cutting techniques or dry techniques accompanied with HEPA filtration.

3.5	REMOVAL OF VINYL ASBESTOS TILE FLOORING

.1	De-activate HVAC system or, subject to Minister's approval, isolate part of HVAC system in affected area.

.2	Provide sheet polyethylene isolation barriers.  Tape over openings in walls, ceilings and floors to prevent the spread of asbestos fibres to other work areas.

.3	Clean contaminated tile to be removed with a damp mop or HEPA vacuum.

.4	Use non-powered hand scrapers to remove floor tile.  Wet floor tile with water sprayer during removal.

.5	Bag contaminated floor tile as it is removed.

.6	After removal, clean removal area with damp mop or HEPA vacuum.

.7	Wet isolation barriers, fold toward inside, sides facing work area.  Prepare for disposal and dispose of as contaminated waste.

3.6	REMOVAL OF VINYL ASBESTOS SHEET FLOORING

.1	Use full containment procedures in accordance with Section 13282, Containment Procedures.

.2	Cover carpet within containment area with minimum 150 micrometer thick sheet polyethylene.  Continuously tape perimeter and joints.

.3	Remove contaminated flooring systematically.  Cut flooring into approximately 600 mm x 600 mm squares.  Carefully peel up squares and place into asbestos disposal bags.

.4	Remove remaining contaminated flooring backing layer as follows:

.1	Wet thoroughly with amended water and let soak for minimum one hour.  Re-wet if drying before removal.

.2	Manually remove backing, using hand scraper and immediately place into asbestos disposal bags.

.3	Leave no remnants adhered to subfloor.

3.7	GLOVEBAG REMOVAL OF PIPE INSULATION

.1	Remove contaminant using glovebag method in accordance with glovebag manufacturer's recommendations and "Manual of Safe Practice".  Take care to avoid cutting glovebags.

.2	Use zippered glovebags as follows:

.1	To remove asbestos material from live feed and condensate steam lines, and other piping transmitting fluids at similar temperatures.

.2	To sequentially remove contaminated material from more than one glovebag length along piping.

.3	Otherwise use either zippered or non-zippered glovebags, at Contractor's option.

.4	When ready to dispose of glovebag, pull disposal bag over glove bag attached to pipe.  Undo zipper to open top of glove bag and fold it down into disposal bag.

.5	When stripping is complete, spray surfaces from which contaminant and contaminated materials have been removed with asbestos sealer to seal any asbestos fibres left on surface.  Ensure surfaces are dry prior to spraying.

.6	Air monitoring in glove bag removal area and a visual inspection by the Minister must be completed prior to acceptance of the work.

3.8	CUT AND WRAP REMOVAL OF INSULATED PIPE FITTINGS

SPEC NOTE:  Asbestos insulation is typically found at pipe fittings, with straight runs often being non-asbestos insulation, e.g., glass fibre.

.1	Remove sections of non-asbestos insulation150-300 mm beyond both ends of asbestos-containing insulation.

.2	Wrap entire contaminated insulated fitting with minimum two layers of 150 micrometre thick sheet polyethylene.  Tape seal joints and around pipe exposed by removal of non-asbestos insulation.

.3	Cut through pipe to permit removal of polyethylene wrapped, insulated fitting.

.4	Clean up contaminated debris using a HEPA filtered vacuum or by wet cleaning.

3.9	REMOVAL OF PIPE AND EQUIPMENT INSULATION - USING

FULL CONTAINMENT PROCEDURES

.1	Remove insulation using full containment procedures in accordance with Section 13282.

.2	Remove insulation in small sections.

.3	Vacuum visible debris from insulation jacket and saturate insulation with amended water.

.4	Cut and remove insulation jacket, applying a mist of amended water to contaminated surfaces as jacket is removed to keep airborne asbestos fibres at the lowest practicable level.  Keep surfaces wet during this operation.

.5	Immediately place contaminated jacket into disposal bag and resoak asbestos insulation.

.6	Where applicable, remove wire mesh holding insulation together.  Dispose of wire mesh as asbestos waste.

3.10	REMOVAL OF ASBESTOS BASE SHEET FROM ASPHALT SHINGLE ROOFS

.1	Remove asphalt shingles and building paper layers.  Avoid disturbing contaminated base sheet.  Discard shingles and building paper as normal construction debris.

.2	Immediately place into asbestos disposal containers, any asbestos base sheet which is disturbed.

.3	Prevent asbestos contaminated material from blowing off the roof.

.4	Starting at ends, remove dry contaminated base sheet material by rolling up the layers.  As the material is rolled up, pick up debris and nails and place into the roll.

.5	Immediately place rolled contaminated base sheet into asbestos disposal containers.

.6	Carefully remove residual mechanically fastened pieces of base sheet and place into asbestos disposal containers.

.7	Apply new asphalt to provide a complete seal over difficult to remove adhered base sheet material.

3.11	ASBESTOS REMOVAL SCHEDULE

| Location | Substrate | Type of Application | Asbestos Type & Percentage | Removal Method |
| --- | --- | --- | --- | --- |
| [ ] | [ ] | [ ] | [ ] | [Full containment] [or] [Glovebag] [ ] |

SPEC NOTE:  Specify locations in terms which are easily identifiable, such as room number, major building areas or other identification methods which are used on drawings to delineate asbestos control area.

SPEC NOTE:  Identify substrate from which asbestos is to be removed, for example:  walls, ceilings, mechanical piping, columns, beams, joists, and underside of decking.

SPEC NOTE:  Identify type of asbestos application which is to be removed, for example:

-Spray Applied Fireproofing

-Pipe Insulation

-Equipment Insulation

SPEC NOTE:  Identify type of asbestos and percentage of material by weight, for example, 30% chrysotile, 10% amosite, 5% crocidolite.

SPEC NOTE:  Specify Contractor options for removal method.  If no option allowed, indicate method to be used.  Coordinate with articles specifying type of material to be removed.

END OF SECTION