Section Cover Page

Section 14 01 42 Lifts for Persons with Physical Disabilities 2008-06-02 Task and Frequency Schedule

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

- Related Sections

- Frequency and Tasks

Every Scheduled Visit

Semi-Annually

1.	Related Sections

.1	Elevator Device Maintenance:	Section 14 01 01.

.2	Preventive Maintenance Log Sheet	Section 14 01 43.

2.	Frequency and Tasks

.1	Every Scheduled Visit:

.1	Meet with Minister’s representative, identify and correct all concerns.

.2	Perform all work required to maintain equipment in safe and reliable operating condition including but not limited to scheduled tasks.

.3	Complete the Minister’s 52-week Work Schedule System Log Sheets and record required information in Log Book.

.2	Semi-Annually:

.1	Runways, pit area, machine area and tops of carriages shall be kept clean and dry.

.2	Stairway runways shall be kept clean and free of obstructions

.3	Inspect and maintain all parts of the machinery and equipment requiring lubrication.

.4	Inspect, clean and maintain all parts of carriage safety mechanisms. Lubricate as required.

.5	Inspect and maintain hydraulic systems including but not limited to valve, seals, packing glands, couplings, piping, hoses, pumps, tanks and oil leakage collection buckets or drip pans.

For units with unexposed hydraulic cylinders, perform a fifteen no-load leak-down test and record result in log book.

.6	Monitor and record hydraulic oil leakage.

.7	Inspect and maintain oil reservoir level.

.8 	Test relief valve setting.

.9	Inspect and maintain all controller components.

.10	Inspect, operate, test and maintain all other mechanical and electrical devices and adjust for proper operation as required.

.11	Test all circuits and parts related to protection in the event of failure.

.12	Inspect and maintain governor and ensure all seals are intact.

.13	Inspect wire ropes.

.14	Inspect and maintain chains and sprockets.

.15	Inspect and maintain all landing and carriage doors or gates and related electrical components, including but not limited to:

.1	interlocks, locks and contacts;

.2	unlocking devices;

.3	vision panels;

.4	self-closing devices; and

.5	opening force test

.16	Inspect , clean and test driving machine brake.

.17	Test carriage emergency lights.

.18	Test and examine all other devices including but not limited to:

.1	audiovisual warning signal;

.2	emergency battery backup system;

.3	power-assisted swing doors and gates;

.4	emergency carriage movement;

.5	levelling tolerances

.6	pressure switch

.7	speed limiting devices;

.8	sensitive edges and surfaces;

.9	chair carriage rotation and foldable seat;

.10	automatic leveling;

.11	alarm and warning signals;

.12	operating devices.

.19	Measure all code-regulated clearances and adjust for compliance as required.

.20	Clean maintain and lubricate reciprocating ball screws. Check ball nut for signs of damage or wear.

.21	Inspect and maintain backup safety nut.

.22	Inspect and maintain acme thread drive screws.

.23	Inspect and maintain rack and pinion drives, chain and chain sprocket drives and rope chain and rope sprocket drives.

END OF SECTION