Section Cover Page

Section 20 05 43 2012-07-01 Identification for Mechanical Systems

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if project: .1 is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

Use this Section to specify mechanical identification requirements.

Identification and labeling of pipes and ducts, is the responsibility of the mechanical subcontractor.  The painting subcontractor is responsible for primary onsite painting of pipes, ducts, and equipment, excluding labels.  The mechanical subcontractor must coordinate with the painting subcontractor to ensure correct colour coding.  Identification requirements are specified accordingly in this Section and in Section 09 91 30 - Painting of Mechanical and Electrical Work.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Data Sheet - Reference Standards

.3	Specification Section Text:

1.	General

1.1	Scope

1.2	Related Requirements

1.3	Related Work Specified in Other Sections

1.4	Quality Control

1.5	Reference Standards

2.	Products

2.1	Identification Labels

2.2	Equipment Identification

2.3	Valve Identification

3.	Execution

3.1	General

3.2	Color Code Schedule

3.3	Height of Legend Letters and Numbers

3.4	Lettering and Direction of Flow Arrow

3.5	Location of Labels

3.6	Visible (Exposed) Ductwork

3.7	Medical Gas Piping Identification

LEED Notes:

Refer to Section 01 35 18 – LEED Requirements for:

.1	Requirements necessary for this project to obtain points required for certification.

.2	Confirmation of LEED prerequisites and credits affecting this Section; not all are mandatory for certification

Maintain built-in sustainability regardless of LEED requirements for:

.1	Recycling, reuse of materials, components and assemblies.

.2	Diversion of construction waste from landfills.

.3	Use of recycled materials, local materials, rapidly renewable and durable materials.

.4	Maintain healthy indoor environment during constructing.

.5	Provide for thermal comfort, access to views and daylight for indoor spaces.

.6	Fostering innovation into facility design and planning.

LEED Credits:

Potential LEED credits available through this section:

Materials and Resources

.1	Credit 2 – Construction Waste Management

Indoor Environmental Quality

.1	Credit 4.2 – Low Emitting Materials: Paints and Coatings

Reference Publications

.1	EMCS Standard for Logical Point Mnemonics

Facility start-up related forms are available from Proforma Contractor Start-Up Report Forms.

These facility start-up forms are available in the Alberta Infrastructure, Technical Resource Centre.

END OF DATA SHEET

1.	General

1.1	scope

.1	Identification for mechanical equipment, piping systems and related components.

1.2	RELATED REQUIREMENTS

.1	Submittals	Division 01

1.3	RELATED WORK SPECIFIED IN OTHER SECTIONS

.1	Refer to and comply with the following sections:

.1	General Mechanical Provisions	Section 20 01 13

.2	Painting of Mechanical and Electrical Work	Section 09 91 30

.3	Pipe and Pipe Fittings	Section 20 20 10

.4	Piping and Equipment Insulation	Section 20 20 30

.5	Medical Gas Systems for Healthcare Facilities	Section 22 60 00

.6	Fire Suppression	Division 21

.7	Plumbing	Division 22

.8	Heating, Ventilation and Air Conditioning	Division 23

1.4	QUALITY CONTROL

.1	Coordinate painting of piping and equipment with work of Section 09 91 30.

.2	Colour Code mechanical equipment, piping and exposed ductwork.  Refer to label identification schedules.

.3	Submit a schedule of pipe and equipment identification methods, materials and colours to the Minister’s representative for review.

1.5	REFERENCE STANDARDS

.1	ASME A13.1 – Scheme for the Identification of Piping Systems.

.2	CAN/CGSB-24.3 – Identification of Piping Systems.

.3	CAN/CSA-B149.1 – Natural Gas Installation Code.

.4	Federal Standard 595C Colours.

.5	WHMIS Pictograms – Workplace Hazardous Materials Information System – GHS (Globally Harmonized System of Classification and Labelling Chemicals) – Pictograms.

2.	Products

2.1	IDENTIFICATION LABELS

.1	Identification Labels for all mechanical piping and ductwork systems, to include:

.1	WHMIS Pictogram (as applicable), same colour as legend letters.

.2	A lettered legend on a coloured background, defining the contents in the pipe, its pressure and temperature and the information necessary to define the hazard.

.3	Arrows to define the direction of flow, same colour as legend letters.

.4	50 mm wide black tape at each end of the label, wrapped around the entire circumference of pipe/insulation to secure the Identification Labels.

.2	Identification Labels may be accomplished by paint, stenciling and/or factory fabricated labels.  Labels shall cover full circumference of pipe or insulation.

2.2	LEGEND LETTERS AND NUMBERS

.1	Height of Legend Letters and Numbers;

Outside Diameter of	Height of Letters	Length of

Pipe or Covering (mm)	and Numbers (mm)	Colour Field (mm)

19 to 32	13	200

38 to 51	19	200

64 to 150	32	300

200 to 250	64	600

Over 250	89	800

.2	Lettering and Direction of Flow Arrow:

.1	Lettering: Capital, Bold, Sans Serif, Century Gothic or Helvetica.

.2	For hazardous piping system: black letters and arrows.

.3	Fire protection, other piping systems and ductwork: white letters and arrows, unless otherwise specified.

2.3	VALVE TAGS, DIRECTORIES AND NAMEPLATES

.1	Valve tags: 40 mm diameter with 20 mm lettering: brass, lamicoid or metal photo black numbers, secured to valve stem with key chain.

.2	Valve Directories: laminated sheets and electronic copy.  Include the following information for each tagged valve:

.1	Valve identified (valve number or logical point mnemonic).

.2	Location.

.3	Service.

.4	Make/model/size and CV for control valves.

.3	Engraved Plastic Nameplates: self-adhesive composite laminated plastic nameplates with one smooth white surface and core of black plastic designed to leave black lettering on a white background.  Engraved lettering height as follows:

.1	All major equipment:  20 mm

.2	Air terminal boxes:  20 mm

.3	Magnetic contactors and VFDs:  20 mm

.4	All other:  8 mm

3.	Execution

3.1	GENERAL

SPEC NOTE: Edit to suit job.

.1	Identify piping systems and ductwork systems with Identification Labels.  Refer to Article 3.2 Identification Schedules.

.2	Identify the location of the following items of equipment which are concealed above a ceiling with Avery “Data Dots”.  The colours shall conform to the following schedule:

HVAC Equipment and duct cleaning access	Yellow

HVAC valves and dampers	Blue

Plumbing equipment and valves	Green

Control dampers and sensors	Black

Fire, smoke, and sprinkler equipment	Red

When T-bar ceilings are installed, adhere “Data Dots” on T-bar framing adjacent to panel to be removed.

3.2	IDENTIFICATION SCHEDULES

.1	Colour numbers for Identification Labels on piping systems, valves and equipment are defined in Federal Standard 595C Colours for colour code identification.

- Black	:	17038

- Yellow	:	13591

- Green	:	14193

- Orange	:	12473

- Brown	:	10115

- Red	:	11350

- White	:	17860

- Aluminum	:	16515

- Blue	:	15180

- Grey	:	16293

- Light Blue	:	15450

- Purple	:	17155

.2	Pipe Identification Label Schedule:

| Service | Background | Lettering | WHMIS Symbol |  | Legend |  |
| --- | --- | --- | --- | --- | --- | --- |
| SPEC NOTE: Edit to suit systems on job. SPEC NOTE: Where (*) is noted, insert appropriate operations condition. |  |  |  |  |  |  |
| Sprinkler | Red | White | N/A |  | WET SPRINKLER |  |
| Wet Stand Pipe | Red | White | N/A |  | WET STANDPIPE |  |
| Dry Stand Pipe | Red | White | N/A |  | DRY STANDPIPE |  |
| Carbon Dioxide (Fire) | Red | White | Yes |  | *[ ]kPa CO2 |  |
| Oxygen | Orange | Black | Yes |  | *[ ]kPa O2 |  |
| Natural Gas | Yellow | Black | Yes |  | *[ ]kPa NATURAL GAS |  |
| Vacuum | Aluminum | Green | Yes |  | VAC. |  |
| Compressed Air | White | Green | Yes |  | *[ ]kPa COMPRESSED AIR |  |
| Service | Background | Lettering | WHMIS Symbol |  | Legend |  |
| Distilled Water | Green | White | Yes |  | DISTILLED WATER |  |
| Domestic Cold Water | Light Blue | White | N/A |  | DOMESTIC COLD WATER |  |
| Domestic Hot Water | Light Blue | White | N/A |  | DOMESTIC HOT WATER |  |
| Domestic Hot Water Recirc. | Light Blue | White | N/A |  | DOMESTIC HOT WATER RECIRC. |  |
| Heating Hot Water Supply | Yellow | Black | N/A |  | *[ ]°C HOT WATER HEATING SUPPLY |  |
| Heating Hot Water Return | Yellow | Black | N/A |  | *[ ]°C HOT WATER HEATING RETURN |  |
| Heating Glycol Supply | Yellow | Black | Yes |  | *[ ]°C HEATING GLYCOL SUPPLY |  |
| Heating Glycol Return | Yellow | Black | Yes |  | *[ ]°C HEATING GLYCOL RETURN |  |
| Chilled Glycol Supply | Green | White | N/A |  | CHILLED GLYCOL SUPPLY |  |
| Chilled Glycol Return | Green | White | N/A |  | CHILLED GLYCOL RETURN |  |
| Chilled Water Supply | Green | White | N/A |  | CHILLED WATER SUPPLY |  |
| Chilled Water Return | Green | White | N/A |  | CHILLED WATER RETURN |  |
| Condenser Water Supply | Green | White | N/A |  | CONDENSER WATER SUPPLY |  |
| Condenser Water Return | Green | White | N/A |  | CONDENSER WATER RETURN |  |
| Plug Load Cooling Water | Green | White | N/A |  | PLUG COOLING WATER SUPPLY |  |
| Plug Load Cooling Water Return | Green | White | N/A |  | PLUG COOLING WATER RETURN |  |
| Service | Background | Lettering | WHMIS Symbol |  | Legend |  |
| Low Pressure Steam | Yellow | Black | Yes |  | *[100] kPa LP STEAM |  |
| High Pressure Steam | Yellow | Black | Yes |  | *[ ] kPa HP STEAM |  |
| Steam Condensate | Yellow | Black | N/A |  | *[ ] kPa HOT STEAM CONDENSATE |  |
| Dry Mop | Aluminum | Green | N/A |  | DRY MOP |  |
| Fuel Oil | Brown | Black | Yes |  | FUEL OIL |  |
| Ammonia | Grey | Black | Yes |  | AMMONIA |  |
| Freon-Liquid | Grey | White | Yes |  | FREON-LIQUID |  |
| Freon-Gas | Grey | White | Yes |  | FREON- GAS |  |
| Carbon Dioxide | Grey | White | Yes |  | *[ ]kPa CO2 |  |
| Lubricating Oil | Brown | White | Yes |  | LUBE OIL |  |
| Engine Exhaust | Aluminum | Black | Yes |  | ENGINE EXHAUST |  |
| Boiler Feed Water | Yellow | Black | N/A |  | HOT BOILER FEED WATER |  |
| Strong Acid | Purple | Black | Yes |  | *ACID [CHEMICAL SYMBOL] |  |
| Nitrogen | Orange | White | Yes |  | *[ ] kPa N2 |  |
| Brine | Green | White | N/A |  | BRINE |  |
| Demineralized Water | Green | White | N/A |  | DEMINERALIZED WATER |  |
| Softened Water | Blue | White | N/A |  | SOFT WATER |  |
| Deionized Water | Blue | White | N/A |  | DEIONIZED WATER |  |
| Chemical Feed Line | Green | Black | Yes |  | *CHEMICAL FEED [CHEMICAL SYMBOL (S03) (P04)] |  |
| Drains | Aluminum | Green | N/A |  | DRAIN |  |
| Vent | Aluminum | Green | N/A |  | VENT |  |
| Service | Background | Lettering | WHMIS Symbol | Legend |  |  |
| Blow Down | Aluminum | Green | N/A | HOT BLOW DOWN |  |  |
| Acetylene | Orange | Black | Yes | *[ ]kPa ACETYLENE |  |  |
| Hydrogen | Orange | Black | Yes | *[ ]kPa H |  |  |
| Carbon Monoxide | Orange | Black | Yes | *[ ]kPa CO |  |  |
| Propane | Orange | Black | Yes | *[ ]kPa PROPANE |  |  |
| Methane | Orange | Black | Yes | *[ ]kPa METHANE |  |  |
| Butane | Orange | Black | Yes | *[ ]kPa BUTANE |  |  |
| Ethane | Orange | Black | Yes | *[ ]kPa ETHANE |  |  |
| Combine Methane Argon | Orange | Black | Yes | *[ ]kPa METHANE/ARGON |  |  |
| Argon Gas | Orange | White | Yes | *[ ]kPa ARGON |  |  |
| Lab Air | White | Green | Yes | *[ ]kPa LAB AIR |  |  |
| Helium | Orange | White | Yes | *[ ]kPa HELIUM |  |  |

.3	Mechanical Equipment Painting:

Heat Exchangers (hot)	Yellow

Heat Exchangers (cold)	Green

Hot Water Storage Tanks	Yellow

Cold Water Storage Tanks	Blue

[                 ]

[                 ]

.4	Ductwork:

- Identify all ductwork with Identification Labels as follows, complete with directional arrows:

Service	Background	Legend	Lettering

Return Air	Blue	RETURN AIR	White

Supply Air	Blue	SUPPLY AIR	White

Mixed Air	Blue	MIXED AIR	White

Combustion Air	Blue	COMBUSTION AIR	White

Relief Air	Blue	RELIEF AIR	White

General Exhaust Air	Blue	GENERAL EXHAUST AIR	White

#### Toilet Exhaust	Blue	TOILET EXHAUST AIR	White

.5	Identify duct access panels with Identification Labels, conforming to the following schedule:

Background	Lettering

Cleaning and service access	Yellow	Black

Controls, including heat sensors	Black	White

Dampers (backdraft, balance and control)	Blue	White

Fire dampers	Red	White

Smoke dampers and detectors	Red	White

.6	Equipment Bases/Housekeeping Pads:

Grey, with 100 mm yellow and black angled bands around edges.

.7	Buried Piping:

Utilize a detectable metallized ribbon laid 150 mm below ground level and above the buried pipe.  Ribbon to display the same information as Identification Labels in intervals not exceeding 800 mm.

3.3	Location of Labels

.1	Orient labels on piping systems in visual sight lines while standing at floor levels.

.2	Locate labels as follows:

.1	Upstream of valves.

.2	Adjacent to changes in direction.

.3	Branches.

.4	Where pipes pass through walls or floors.

.5	On straight pipe runs at 6 m intervals.

.6	For natural gas and propane piping systems, at 6 m intervals on straight pipe runs.

.7	Where system is installed in pipe chases, ceiling spaces, shafts, or similar confined spaces, at entry and exit points and at access openings

.8	At beginning and end points of each run and at each piece of equipment.

.3	Adhere labels to piping/insulation.  Labels to cover entire pipe circumference.  Secure both ends of labels with 50 m wide black tape around the entire pipe circumferences.

3.4	Visible (exposed) ductwork

.1	Pain visible ductwork as directed by Architect.  Refer to Section 09 91 00.

.2	Paint ductwork/flexible connectors that are visible behind grilles/diffusers, matt black.  Refer to Section 09 91 00.

3.5	MEDICAL GAS PIPING IDENTIFICATION

.1	Refer to Section 22 66 00.

3.6	MECHANICAL CONTROL IDENTIFICATION

.1	Refer to Section 23 09 28, EMCS Fieldwork.

3.7	RECORD PROVISIONS

.1	Mark valve numbers on Red Line system schematic drawings for transfer onto record drawings.  Include copies of Operation and Maintenance Manuals.

3.8	VALVE TAGS

.1	Tag pneumatic/electric controls, instruments and relays.  Key to control schematics on which instruments are numbered in sequence.

.2	Tag all valves in mechanical rooms.

.3	Tag all control valves external to mechanical rooms.  This includes control valves on radiant panels, perimeter radiation and air terminal boxes.

.4	Tag all circuit balancing and isolating valves external to mechanical rooms except valves at terminal heating and cooling equipment.

.5	Identify and tag pneumatic/electric thermostats relating to terminal unit and valve numbers.

3.9	VALVE DIRECTORIES

.1	Include laminated directories in operation and maintenance manuals.  Also provide electronic copy in PDF, as well as spreadsheet user editable format.

3.10	NAMEPLATES

.1	Identify the following with engraved plastic nameplates:

.1	All mechanical equipment.

.2	Air terminal boxes, VFDs.

.3	Pneumatic/electric thermostats.

.4	Electric starting switches, electric disconnects, remote push buttons and control panels.

.2	All nameplates to be mechanically fastened, easily visible without need to use ladder or extraordinary body position.  Affix additional nameplates if necessary.

.3	Provide the Minister with an example of the contents of each type of nameplate.  Obtain approval prior to engraving.

END OF SECTION