Section Cover Page

Section 20 05 43 2008-05-01 Mechanical Identification

Use this Section to specify mechanical identification requirements.

Under Alberta Construction Tendering System, Trade Definitions, identification and labelling including secondary colour coding (banding) of pipes and ducts, is the responsibility of the mechanical subcontractor.  Painting subcontractor is responsible for primary onsite painting of pipes, ducts, and equipment, excluding labels and secondary banding.  The mechanical subcontractor must coordinate with the painting subcontractor to ensure correct colour coding.  Identification requirements are specified accordingly in this Section and in Section 09 91 30 - Painting of Mechanical and Electrical Work.

This section does not include information on EMCS systems.  Refer the Basic Master Specification, Section 20 05 53 when the project has these systems.

This Master Specification Section contains:

.1	This Cover Page

.2	Specification Section Text:

1.	General

1.1	Related Sections

1.2	Reference Document

2.	Products

2.1	Tags, Labels and Banding

2.2	Valve Tag Directory

3.	Execution

3.1	Labelling

3.2	Tagging

3.3	Location Identification

3.4	Directories

3.5	Secondary Colour Banding for Mechanical Piping

1.	General

1.1	RELATED SECTIONS

.1	Site painting of mechanical work:	Section 09 91 30

1.2	REFERENCE DOCUMENT

.1	Comply with requirements of latest edition of "APWSS Colour Coding Requirements for Mechanical and Electrical Systems", hereinafter referred to as "APWSS Colour Coding Requirements".

SPEC NOTE:   This reference document is available from Procurement Section, Alberta Infrastructure, 3rd Floor, 6950 - 113 Street, Edmonton;  Telephone:  (780) 422-7620.

.2	Obtain copy of APWSS Colour Coding Requirements document from the Minister prior to starting work.

2.	Products

2.1	TAGS, LABELS AND BANDING

.1	Valve Tags:  tags with 12 mm high lettering and brass jack chain for fastening to valve.  Following types of valve tags are acceptable:

.1	Brass tags:  40 mm diameter.

.2	Fiberglass tags:  50 mm x 50 mm.

.3	Anodized aluminum tags:  40 mm diameter.

.2	Laminated Plastic Nameplate:  self-adhesive composite laminated plastic nameplates with one smooth white surface and core of black plastic.  Designed to leave black lettering on a white background when engraved.

.1	Mechanical Equipment:  engraved lettering 20 mm high.

.3	Colour Banding Tape:  adhesive backed plastic tape, integrally coloured.

.4	Identification Labels:  adhesive backed plasticized labels, yellow colour, with:

.1	Legends consisting of black lettering, minimum 50 mm high.

.2	Black direction of flow arrows.

.5	Stencils:  50 mm high black lettering and flow arrows.

2.2	VALVE TAG DIRECTORY

.1	Provide two copies of the typewritten valve tag directory.

.2	Mount one directory in a metal frame and protect with acrylic sheet and place the second copy in the maintenance manual.

.3	Include following information in directory:

.1	Valve number

.2	Location

.3	Service

.4	Make/model size

.5	With/without handwheel

.6	Type of control

3.	Execution

3.1	LABELLING

.1	Use identification labels or stencils to apply legends and direction of flow arrows, as detailed in APWSS Colour Coding Requirements, and as follows:

.1	Apply to full colour coded mechanical piping and to mechanical ductwork in sufficient numbers of locations to provide easy identification. Include crawlspace locations, boiler room and mechanical rooms.

.2	Apply to intermittent colour coded mechanical piping wherever colour coding bands occur.

.2	Adhere labels with sufficient coat of contact cement to ensure permanent adhesion.  Seal with two coats of clear lacquer.

.3	Identify major mechanical equipment with laminated plastic nameplates.

.4	Identify electric starting switches, electric disconnects and remote push buttons with laminated plastic nameplates.

3.2	TAGGING

.1	Tag automatic controls, instruments and relays.  Key to control schematics on which instruments and numbered in sequence. Include all new and existing valves with a new numbering system on renovation projects.

.2	Tag all valves in mechanical rooms, and all circuit balancing and isolating valves external to mechanical room except valves at terminal heating equipment.

.3	Identify and tag radiator valves with numbers.

3.3	LOCATION IDENTIFICATION

.1	Provide equipment, valve and damper location tacks or adhesive disks in T-bar type ceilings, colour coded as follows:

.1	Yellow - HVAC Equipment

.2	Red - Fire Dampers/Smoke Dampers

.3	Green - Plumbing Valves

.4	Blue - Heating/Cooling Valves.

.2	Locate tacks or disks in corner of T-bar panel closest to equipment.

3.4	DIRECTORIES

.1	Install valve tag directory on wall in mechanical room.

3.5	SECONDARY COLOUR BANDING FOR MECHANICAL PIPING

.1	Full Colour Coded Piping:  apply 50 mm wide secondary colour banding tape over primary colour coded piping identifying hazard level for each type of service, where applicable, in accordance with APWSS Colour Coding Requirements.  Apply to piping in sufficient numbers of locations to provide easy identification.

.2	Intermittent Colour Coded Piping:  apply 50 mm wide secondary colour banding tape on intermittent colour coded piping to identify hazard level for each service, where applicable. Apply over 450 mm long primary colour coding bands, as detailed in APWSS Colour Coding Requirements.

END OF SECTION