Section Cover Page

Section 20 05 48 2010-12-01 Vibration Isolation

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Reference Standard

1.2	Submittals

1.3	General Requirements

1.4	Inspection

2.	Products

2.1	Inertia Bases

2.2	Vibration Isolators

3.	Execution

3.1	Application

3.2	Installation

3.3	Performance

3.4	Isolation Schedule

1.	General

1.1	REFERENCE STANDARD

.1	Provide and install mechanical equipment so that Average Noise Criteria Curves, as outlined in ASHRAE Guide, are not exceeded.

1.2	SUBMITTALS

.1	Provide vibration isolation shop drawings showing isolator locations, load on each isolator, inertia slab dimensions.

1.3	GENERAL REQUIREMENTS

.1	Supply vibration isolation equipment and materials by one supplier.  Consider side loading of equipment and inertia bases when calculating maximum loads on isolators.

.2	Ensure equipment is sufficiently rigid for isolator point loading.

1.4	INSPECTION

.1	Provide inspection services by vibration isolation equipment and materials manufacturer's representative for final installation and provide written report that installation is in accordance with specifications and manufacturer's recommendations.

2.	Products

2.1	INERTIA BASES

.1	Type A:  Integral structural steel fan and motor base with motor slide rails.

.2	Type B:  Slung structural steel base with gussetted brackets.

.3	Type C:  Reinforced 20 MPa concrete base with full depth perimeter structural channel frame, with gussetted brackets and anchor bolts.

.4	Type D:  Reinforced 20 MPa concrete base with chamfered edges without channel frame.

2.2	VIBRATION ISOLATORS

.1	Type 1:  Closed spring mount with top and bottom housing separated with neoprene rubber stabilizers.

.2	Type 2:  Open spring mount with iso-stiff springs (horizontal stiffness equal to vertical stiffness).

.3	Type 3:  Open spring mount with iso-stiff springs, heavy mounting frame and limit stop.

.4	Type 4:  Closed spring mount with iso-stiff springs and limit stop.

.5	Type 5:  Closed spring hanger with acoustic washer.

.6	Type 6:  Closed spring hanger with 25 mm thick acoustic isolator.

.7	Type 7:  Elastomer mount with threaded insert and hold down holes.

.8	Type 8:  Neoprene jacketed pre-compressed moulded fiberglass.

.9	Type 9:  Rubber waffle pads, 30 durometer, minimum 12 mm thick, maximum loading 280 kPa.  Use neoprene in oily locations or outdoors.

.10	Type 10:  Rubber-steel-rubber pads, 12 mm thick rubber waffle pads bonded to 6 mm thick steel plate.

.11	Provide pairs of neoprene side snubbers or restraining springs where side torque or thrust may develop.

.12	Colour code spring mounts, springs selected to operate at no greater than 2/3 solid deflection and have 6 mm ribbed neoprene pads.

3.	Execution

3.1	APPLICATION

.1	Provide vibration isolators for mechanical motor driven equipment throughout, unless specifically noted otherwise.

3.2	INSTALLATION

.1	Set steel bases for 15 mm clearance between housekeeping pad and base.  Set concrete inertia bases for 50 mm clearance.  Adjust equipment level.

.2	Provide spring isolators on piping connected to isolated equipment as follows:  up to 100 mm diameter, first 3 points of support; 125 mm to 200 mm diameter, first 4 points of support; 250 mm diameter and over, first 6 points of support.  Static deflection of first point shall be twice deflection of isolated equipment.

3.3	PERFORMANCE

.1	Install inertia bases of type and thickness, and isolators of type and static deflection as indicated on Isolation Schedule.

3.4	ISOLATION SCHEDULE

|  | Base | Isolation |
| --- | --- | --- |
| Isolated Equipment | Type | Thickness | Type | Deflection |

END OF SECTION