Section Cover Page

Section 20 20 10 2010-12-01 Pipe and Pipe Fittings

Use this Section to specify pipe and pipe fittings for mechanical services and systems, with some notable exceptions.  For guidelines on Section scope, refer to Article 1.1, Section Includes, and Article 1.3, Related Sections, in Specification Section text.

This Section includes most piping systems commonly required in commercial and institutional buildings.  It is not an exhaustive list and must be expanded if additional piping systems are required.

This Master Specification Section contains:

1.	This Cover Sheet

2.	Specification Section Text:

1.	General

1.1	Section Includes

1.2	Related Requirements

1.3	Related Sections

1.4	Alternatives

1.5	Reference Documents

1.6	References

1.7	Welding Qualifications

1.8	Welding Procedures

1.9	Contractor's Quality Control

1.10	Coordination

2.	Products

2.1	Steel Pipe System Components

2.2	Pressfitting Pipe System Components

2.3	Cast Iron Soil Pipe Components

2.4	Epoxy Coated Cast Iron Soil Pipe Components

2.5	Copper Pipe Components

2.6	ABS Pipe Components

2.7	PVC Pipe Components

2.8	Unions and Flanges

3.	Execution

3.1	Installation Requirements

3.2	Routes and Grades

3.3	Steel Piping System - General

3.4	Steel Piping System - Teeing Off Main Line

3.5	Pressfitting System

3.6	Non-Ferrous Piping Connections

3.7	Copper Pipe - Mechanically Formed Connections

3.8	Unions and Flanges

3.9	Gas Piping

3.10	Oil Piping

3.11	Piping Schedule

Applicable Regulations:

.1 	National Plumbing Code of Canada 2005.

.2 	Alberta Regulation 119/2007 – Plumbing Code Regulation.

.3 	Provincial Board of Labour Regulations for Welded Steel precision tubing as approved by the authority having jurisdiction.

END OF DATA SHEETS

1.	General

1.1	SECTION INCLUDES

.1	This Section includes requirements for pipe and pipe fittings for all mechanical services and systems, inside and outside building perimeter, except:

.1	Services and connections provided by a utility.

.2	[Domestic water] [storm sewer] [and] [sanitary sewer] services from 1.5 m outside building perimeter to utility connection point.

.3	[Sprinkler system.]

.4	[Standpipe and hose system.]

.5	[                  ].

SPEC NOTE:  List all other services and systems for which pipe and pipe fittings are specified elsewhere.

1.2	RELATED REQUIREMENTS

.1	Mechanical General Requirements:	Section 20 00 13.

1.3	RELATED SECTIONS

.1	Mechanical and Electrical Service Connections:	Division 01.

.2	Standpipe Pipe:	Section 21 12 00.

.3	Sprinkler Pipe:	Section 21 13 10.

.4	Piped Utilities:	Division 33.

.5	[             ]:	Section [    ].

1.4	ALTERNATIVES

.1	Pipe and pipe fitting products are specified by system in Piping Schedule at end of this Section.  Unless otherwise specified, where schedule specifies more than one type of material for a single system, select any one of the specified alternative materials.

1.5	REFERENCE DOCUMENTS

.1	American Society of Mechanical Engineers (ASME):

| .1 | ASME B16.18-2001 | Cast Copper Alloy Solder Joint Pressure Fittings |
| --- | --- | --- |
| .2 | ANSI/ASME B16.22-2001 | Wrought Copper and Copper Alloy Solder Joint Pressure Fittings |
| .3 | ASME B16.3-2006 | Malleable - Iron Threaded Fittings: Classes 150 and 300 |
| .4 | ASME B16.5-2009 | Pipe Flanges and Flanged Fittings, NPS 1/2 Through NPS 24 – Metric/Inch Standard |
| .5 | ASME B16.25-2007 | Buttwelding Ends |
| .6 | ASME B16.39-2009 | Malleable Iron Threaded Pipe Unions Classes 150, 250 and 300 |
| .7 | ASME B31.1-2007 | Power Piping |
| .8 | ASME B31.3-2008 | Process Piping |
| .9 | ASME B31.5-2010 | Refrigeration Piping and Heat Transfer Components |
| .10 | ANSI/ASME B16.9-2007 | Factory-Made Wrought Steel Buttwelding Fittings |
| .11 | ASME Section IX | Welding and Brazing Qualifications |

.2	American Society for Testing and Materials (ASTM):

| .1 | ASTM A53/A53M-10 | Pipe, Steel, Black and Hot-Dipped, Zinc-Coated Welded and Seamless |
| --- | --- | --- |
| .2 | ASTM A106/A106M-10 | Seamless Carbon Steel Pipe for High-Temperature Service |
| .3 | ASTM 214/A214M -96(2005) | Electric Resistance-Welded Carbon Steel Heat-Exchanger and Condenser Tubes |
| .4 | ASTM B32-08 | Solder Metal |
| .5 | ASTM B88-09 | Seamless Copper Water Tube |
| .6 | ASTM B280-08 | Seamless Copper Tube for Air Conditioning and Refrigeration Field Service |
| .7 | ASTM B306-09 | Copper Drainage Tube (DWV) |
| .8 | ASTM B664-90(2006) | 80% Silver - 20% Graphite Sliding Contact Material |
| .9 | ASTM C564-09a | Rubber Gaskets for Cast Iron Soil Pipe and Fittings |
| .10 | ASTM D1002-10 | Apparent Shear Strength of Single-Lap-Joint Adhesively Bonded Metal Specimens by Tension Loading (Metal-to-Metal) |
| .11 | ASTM D2235-04 | Solvent Cement for Acrylonitrile-Butadiene-Styrene (ABS) Plastic Pipe and Fittings |
| .12 | ASTM D2464-06 | Threaded Poly(Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 80 |
| .13 | ASTM D2564-04(2009)e1 | Solvent Cements for Poly (Vinyl Chloride) PVC Plastic Piping Systems |
| .14 | ASTM D3138-04 | Solvent Cements for Transition Joints Between Acrylonitrile-Butadiene-Styrene (ABS) and Poly (Vinyl Chloride) (PVC) Non-Pressure Piping Components |
| .15 | ASTM G17-07 | Test Method for Penetration Resistance of Pipeline Coatings (Blunt Rod) |

.3	Canadian Gas Association (CGA):

| .1 | CAN/CGA B149.1-05 | Natural Gas and Propane Installation Code |
| --- | --- | --- |

.4	Canadian Standards Association (CSA):

| .1 | CSA B52-05 | Mechanical Refrigeration Code |
| --- | --- | --- |
| .2 | CAN/CSA-B70-06 | Cast Iron Soil Pipe, Fittings and Means of Joining |
| .3 | CSA B139-09 | Installation Code for Oil Burning Equipment |
| .4 | CAN/CSA-B181.1-06 | ABS Drain, Waste and Vent Pipe and Pipe Fittings (Published in CAN/CSA-B1800-06) |
| .5 | CAN/CSA-B181.2-06 | PVC Drain, Waste and Vent Pipe and Pipe Fittings (Published in CAN/CSA-B1800-06) |

1.6	REFERENCES

.1	Fabricate systems in accordance with the following fabrication standards:

.1	Flanged, welded steel piping systems:

.1	Butt welded ends:  to ASME B16.25.

.2	Steel pipe flanges:  to ASME B16.5.

.2	Steam Systems:

.1	Operating at 930 kPa or less:  to ASME B31.1.

.2	Operating at 930 kPa or over:  to ASME B31.3.

.3	Natural Gas and Propane:

.1	Natural gas and propane vapour phase, up to 70 kPa:  to ASME B31.3

.2	Propane, liquid phase:  to ASME B31.3.

.4	Refrigerant System:  to ASME B31.5.

1.7	WELDING QUALIFICATIONS

.1	Conform to ASME Section IX and Alberta Labour Regulations.

1.8	WELDING PROCEDURES

.1	Conform to ASME B31.1, ASME B16.25 and ASME Section IX.

1.9	CONTRACTOR'S QUALITY CONTROL

.1	Provide specified quality control for the following joint systems:

.1	Mechanically formed connections in copper pipe.

.2	Pressfitting system.

.3	Mechanical grooved coupling and fitting system.

.2	Arrange and pay for site services of joint system supplier or proponent to:

.1	Instruct on the correct use of the system.

.2	Inspect [ten] [       ] random samples of installed joints.

SPEC NOTE:  Modify the number of random sample joints to be taken to suit the size of the project.

.3	Submit a report describing findings of the inspection to the Minister.

1.10	COORDINATION

.1	Coordinate piping installation routes and elevations with installation of sprinkler, sheet metal and electrical work.

2.	Products

2.1	STEEL PIPE SYSTEM COMPONENTS

.1	Pipe:

.1	Black Steel, Schedule 40:  electric resistance welded, ASTM A53, Grade B.

.2	Black Steel, Schedule 80:  electric resistance welded, ASTM A53, Grade B.

.3	Galvanized Steel, Schedule 40:  electric resistance welded, ASTM A53, Grade B.

.2	Joint and Fitting Components:

.1	Threaded Fittings:  malleable iron to ASME B16.3.

.2	Welded Fittings:  wrought steel, butt welding type to ANSI/ASME B16.9.

.3	Mechanical Grooved Couplings:  ductile or malleable iron housing, synthetic rubber gasket of central cavity pressure-responsive design; with nuts, bolts, locking pin, locking toggle, or lugs to secure grooved pipe and fittings.

.4	Mechanical Grooved Fittings:  to ASTM A106M, steel fittings with grooves or shoulders designed to accept grooved end couplings.

2.2	PRESSFITTING PIPE SYSTEM COMPONENTS

.1	Pressfitting Pipe:  mild steel, electric resistance welded precision thin walled tubing to ASTM A214M, suitable for working pressure of 1600 kPa at 100°C.

.2	Pressfitting Connection:  mild steel fitting, rubber "O" ring seal, designed to provide a permanent fluid tight connection.

2.3	CAST IRON SOIL PIPE COMPONENTS

.1	Pipe:  cast iron soil pipe to CAN/CSA-B70.

.2	Mechanical Joint Components:  hubless fittings, elastomeric gaskets and stainless steel mechanical joint couplings to CAN/CSA-B70.

2.4	EPOXY COATED CAST IRON SOIL PIPE COMPONENTS

.1	Pipe:  epoxy coated cast iron soil pipe to CAN/CSA-B70.

.2	Mechanical Joint Components:  hubless fittings, elastomeric gaskets and stainless steel mechanical joint couplings to CAN/CSA-B70.

.3	Epoxy Coating:  interior surfaces of cast iron pipe and fittings coated with 250 um fusion bonded epoxy, meeting the following requirements:

.1	Adhesion:  to ASTM D1002.

.2	Penetration Resistance:  to ASTM G17.

2.5	COPPER PIPE COMPONENTS

.1	Pipe:

.1	Copper Water Tube:  to ASTM B88.

.2	ACR Copper Tube:  to ASTM B280.

.3	DWV Copper Tube:  to ASTM B306.

.2	Joint and Fitting Components:

.1	Wrought Copper Fittings:  to ANSI/ASME B16.22.

.2	Cast Copper, Brass & Bronze Fittings:  to ASME B16.18.

.3	Solder Joints:  to ASTM B32.

.4	Brazed Joints:  to ASTM B664.

2.6	ABS PIPE COMPONENTS

.1	Pipe:  ABS Plastic Pipe:  to CAN/CSA-B181.1.

.2	Joint and Fitting Components:

.1	Fittings:  ABS fittings to CAN/CSA-B181.1.

.2	ABS Solvent Cement:  to ASTM D2235.

.3	ABS - PVC Solvent Cement:  to ASTM D3138.

2.7	PVC PIPE COMPONENTS

.1	Pipe:  PVC plastic pipe to CAN/CSA-B181.2.

.2	Joint and Fitting Components:

.1	Fittings:  PVC fittings to CAN/CSA-B181.2.

.2	PVC Solvent Cement:  to ASTM D2564.

.3	ABS-PVC Solvent Cement:  to ASTM D3138.

2.8	UNIONS AND FLANGES

.1	Pipe size 50 mm and smaller:  1035 kPa and as follows:

.1	Ferrous piping:  malleable iron unions with bronze to iron ground joint to ASME B16.39.

.2	Copper piping:  bronze unions.

.2	Pipe size 65 mm and larger:  1035 kPa and as follows:

.1	Ferrous piping:  forged steel slip-on flanges to ASME B16.5 with 1.6 mm thick preformed neoprene bonded to asbestos for general applications, neoprene gasket for gas service.

.2	Copper piping:  bronze flanges.

3.	Execution

3.1	INSTALLATION REQUIREMENTS

.1	Install piping systems in accordance with the following:

.1	Natural gas and Propane distribution system:  to CAN/CGA B149.1 and Alberta amendments.

.2	Oil burning equipment installation:  to CSA B139.

.3	Plumbing and drainage system:  to National Building Code of Canada 2005 and Alberta Regulation 119/2007 – Plumbing Code Regulation.

.4	Heating and cooling system:  to comply with recommendations of ASHRAE Guide.

.5	Refrigeration system:  to CSA B52.

.2	Install piping to allow for expansion and contraction without exceeding maximum allowable stresses for pipe and equipment flanges.

.3	Provide clearance for proper installation of insulation and for access to valves, air vents, drains and unions.

.4	Provide all offsets necessary to install piping systems within the physical limitations of the building.

3.2	ROUTES AND GRADES

.1	Route piping in an orderly manner and maintain proper grades.

.2	Install piping to conserve headroom and space.

.3	Route above grade piping parallel to walls.

.4	Where practicable, group piping at common elevations.

.5	Install concealed pipes close to building structure to keep furring to a minimum.

.6	Slope hydronic and domestic water system piping at 0.2% and drain at low points.

.7	On closed loop water systems, equip low points with 20 mm drain valves and hose nipples.  At high points, provide collecting chambers and high capacity float operated automatic air vents.

.8	Slope steam piping at 0.5% and condensate piping at 0.7% down in direction of flow.  Provide drip trap assembly at low points and at points where condensate may collect in front of control valves.  Where condensate lines form a trap, provide vent loop over trapped section.

.9	Make reductions in water, steam and condensate piping with eccentric reducing fittings to provide complete drainage and venting.

.10	Grade horizontal sanitary and storm drainage vent piping at 2% minimum.

3.3	STEEL PIPING SYSTEM - GENERAL

.1	Use mechanical grooved couplings and fittings in accessible locations only.

.2	Use only long radius elbows.

.3	Ream piping and tubing.  Clean off scale and dirt inside and outside before assembly.  Remove welding slag or other foreign material from piping.

.4	Protect galvanized pipe threads with pipe paste.

3.4	STEEL PIPING SYSTEM - TEEING OFF MAIN LINE

.1	Mains 150 mm and smaller:

.1	Use saddle type connections where main is at least one size larger than branch.

.2	Use direct connection where branch is at least three sizes smaller than main.

.2	Mains 200 mm and larger:

.1	Use saddle type connections where main is at least two sizes larger than branch.

.2	Use direct connection for branches 65 mm and smaller.

.3	Do not project branch pipe inside main line.

3.5	PRESSFITTING SYSTEM

.1	Install pressfitting system in accordance with system manufacturers instructions.

3.6	NON-FERROUS PIPING CONNECTIONS

.1	Use non-toxic joint compound on potable water lines.

.2	Provide non-conducting type connections wherever joining dissimilar metals.  Brass adaptors and valves are acceptable.

.3	Sleeve copper piping buried under building so that pipe can move freely; joints are not allowed in piping buried under building.

3.7	COPPER PIPING - MECHANICALLY FORMED CONNECTIONS

.1	Mechanically formed tee connections with brazed joints may be used in lieu of tee fittings in copper tubing provided they meet the following:

.1	Size and wall thickness of main tube and branch tube are listed by manufacture of forming equipment as an acceptable application.

.2	Height of drawn collar is not less than three times wall thickness of main tubing.

.3	End of branch tube is notched to conform to inner curve of tube and dimpled to set exact penetration depth into collar.

.4	Resulting joint is brazed and is minimum of three times as long as thickness of thinner joint member.

3.8	UNIONS AND FLANGES

.1	Make connections to equipment and branch mains with unions or flanges.

.2	Use 1.5 mm thick preformed synthetic rubber asbestos gaskets for flanged connections for all services except gas.

.3	Gas Service:

.1	Air test unions used for gas service.

.2	Use synthetic rubber gaskets for flanged connections.

3.9	GAS PIPING

.1	Use isolating gas cocks on primary gas line installed with isolating union at outlet.

.2	Band interior gas piping to electrical system ground conductor to maintain gas piping at electrical system ground.

.3	For buried piping, use piping with factory or site applied 250 µm thick polyethylene jacketing.

.4	Apply heat shrink plastic jacketing to joints on buried piping.

.5	Install gas piping in open or ventilated spaces.  Pitch lines and provide drip legs for condensation and dirt at appliance connection.  Where gas piping is run in a concealed space, provide ventilation grilles to CAN/CGA B149.1.

3.10	OIL PIPING

.1	For buried piping, use piping with factory or site applied 250 µm thick polyethylene jacketing.

.2	Apply heat shrink plastic jacketing on all joints on buried piping.

3.11	PIPING SCHEDULE

| System | Pipe | Fitting | Joint |
| --- | --- | --- | --- |
| Hydronic heating | Black steel | Threaded | Screwed |
| and cooling | Schedule 40, |  |  |
| up to 120°C | 50 mm or less | Welding | Welded |
| and 1035 kPa |  |  |  |
|  |  | Mechanical | Clamped |
|  |  | grooved |  |
|  | Black steel, | Welding | Welded |
|  | Schedule 40, |  |  |
|  | greater than | Mechanical | Clamped |
|  | 50 mm | grooved |  |
|  | Pressfitting | Pressfitting | Compression |
|  | 50 mm or less |  |  |
|  | Copper water tube | Wrought | Soldered, |
|  | type L, | copper | 95-5 |
|  | Drawn temper |  | tin-antimony |
|  |  | Cast copper | Soldered, |
|  |  |  | 95-5 |
|  |  |  | tin-antimony |
| Condenser water | Black steel, | Threaded | Screwed |
|  | Schedule 40, |  |  |
|  | 50 mm or less | Welding | Welded |
|  |  | Mechanical | Clamped |
|  |  | grooved |  |
|  | Black steel, | Welding | Welded |
|  | Schedule 40, |  |  |
|  | greater than | Mechanical | Clamped |
|  | 50 mm | grooved |  |

Continued next page

3.11	PIPING SCHEDULE (Cont'd)

| System | Pipe | Fitting | Joint |
| --- | --- | --- | --- |
|  | Copper water tube | Drawn cast | Soldered, |
|  | type L, | brass | 95-5 |
|  | drawn temper |  | tin-antimony |
|  |  | Wrought copper | Soldered, |
|  |  |  | 95-5 |
|  |  |  | tin-antimony |
| Low pressure | Black steel, | Threaded | Screwed |
| steam | Schedule 40 |  |  |
|  | 50 mm or less | Welding | Welded |
|  | Black steel, | Welding | Welded |
|  | Schedule 40 |  |  |
|  | Greater than 50 mm |  |  |
| Steam condensate | Black steel, | Threaded | Screwed |
| up to 1035 kPa | Schedule 80 |  |  |
|  | 50 mm or less | Welding | Welded |
|  | Black steel, | Welding | Welded |
|  | Schedule 80 |  |  |
|  | greater than 50 mm |  |  |
| Equipment drains | Galvanized steel, | Galvanized | Screwed |
| and overflows | Schedule 40, | threaded |  |
|  | ASTM A53-96 only |  |  |
|  | Copper water tube, | Wrought | Soldered, |
|  | Type L, | copper | 95-5 |
|  | drawn temper |  | tin-antimony |
| Refrigerant | ACR copper | Wrought copper | Brazed |
| freon |  |  |  |
|  |  | Cast copper | Brazed |

Continued next page

3.11	PIPING SCHEDULE (Cont'd)

| System | Pipe | Fitting | Joint |  |
| --- | --- | --- | --- | --- |
| Domestic water | Copper water tube | Wrought | Soldered, |  |
| above grade | type L, | copper | 95-5 |  |
|  | drawn temper |  | tin-antimony |  |
|  |  | Cast copper | Soldered, |  |
|  |  |  | 95-5 |  |
|  |  |  | tin-antimony |  |
| [Compressed air] | Galvanized steel, | Galvanized, | Screwed |  |
| [Vacuum] | Schedule 40, | threaded |  |  |
|  | ASTM A53-96 only |  |  |  |
|  | Copper water tube | Wrought | Soldered, |  |
|  | type L, | copper | 95-5 |  |
|  | drawn temper |  | tin-antimony |  |
|  |  | Cast copper | Soldered, |  |
|  |  |  | 95-5 |  |
|  |  |  | tin-antimony |  |
| DWV above grade | Cast iron | Hubless | Clamped |  |
| and buried |  | cast iron |  |  |
|  | DWV copper | Cast bronze | Soldered, |  |
|  | (above grade only) |  | 50-50 |  |
|  |  |  | tin-lead |  |
|  |  | Wrought | Soldered, |  |
|  |  | copper | 50-50 |  |
|  |  |  | tin-leaded |  |
|  | ABS | ABS | Solvent |  |
|  |  |  | welded |  |
|  | PVC | PVC | Solvent |  |
|  |  |  | welded |  |

Continued next page

3.11	PIPING SCHEDULE (Cont'd)

| System | Pipe | Fitting | Joint |
| --- | --- | --- | --- |
| Storm sewer, | Cast iron | Hubless | Clamped |
| above grade |  | cast iron |  |
|  | DWV copper | Cast bronze | Solder, |
|  |  |  | 50-50 |
|  |  |  | tin-lead |
|  |  | Wrought | Solder, |
|  |  | copper | 50-50 |
|  |  |  | tin-lead |
|  | ABS | ABS | Solvent |
|  |  |  | welded |
|  | PVC | PVC | Solvent |
|  |  |  | welded |
| Special waste | Epoxy coated | Hubless | Clamped |
|  | cast iron | cast iron |  |
|  | ABS | ABS | Solvent |
|  |  |  | welded |
|  | PVC | PVC | Solvent |
|  |  |  | welded |
| Natural gas | Black steel, | Threaded | Screwed |
| low pressure | Schedule 40 |  |  |
| less than 1400 | 50 mm or less | Welding | Welded |
| kPa, inside |  |  |  |
| building |  |  |  |
|  | Black steel, | Welding | Welded |
|  | Schedule 40 |  |  |
|  | greater than |  |  |
|  | 50 mm |  |  |

Continued next page

3.11	PIPING SCHEDULE (Cont'd)

| System | Pipe | Fitting | Joint |
| --- | --- | --- | --- |
| Natural gas | Black steel, | Welding | Welded |
| high pressure | Schedule 40, |  |  |
| greater than | ASTM A53-96 |  |  |
| 1400 kPa, inside | Grade B only |  |  |
| building |  |  |  |
| Oil piping | Black steel, | Threaded | Screwed |
|  | Schedule 40 |  |  |
|  |  | Welding | Welded |

# END OF SECTION