Section Cover Page

Section 20 20 30 2008-05-01 Piping and Equipment Insulation

Use this Section to specify requirements for Piping and Equipment Insulation.

This Master Specification Section contains:

.1	This Cover Page

.2	Data Sheet - Reference Documents

.3	Specification Section Text:

1.	General

1.1	Related Requirements

1.2	Product Options and Substitutions

1.3	Shop Drawings and Product Data

1.4	Definitions

1.5	Flame/Smoke Development Ratings

2.	Products

2.1	Hot Pipe Insulation

2.2	Hot Equipment Insulation

2.3	Cold Pipe Insulation

2.4	Cold Equipment Insulation

2.5	Accessories

2.6	Recovery Materials

3.	Execution

3.1	Installation, General

3.2	Hot Pipe Insulation Application

3.3	Hot Equipment Insulation Application

3.4	Cold Pipe Insulation Application

3.5	Cold Equipment Insulation Application

3.6	Insulation Type Thickness Schedule

Consider carefully all requirements relating to recovering of exposed insulation surfaces.  Specify recovering materials as follows:

.1	Canvas:  if surfaces are to be painted.

.2	PVC:  if surfaces are subject to damage or abuse.

.3	Aluminum:  if surfaces are subject to damage or abuse or where appearance is important.

Applicable Standards:

.1	ASTM C411-82 (1992)	Hot-Surface Performance of High Temperature Thermal Insulation.

.2	ASTM E84-96a	Surface Burning Characteristics of Building Materials

.3	CAN/CGSB-51.9-92	Mineral Fibre Thermal Insulation For Piping and Round Ducting.

.4	CAN/CGSB-51.10-92	Mineral Fibre Board Thermal Insulation

.5	CGSB 51.11-92	Mineral Fibre Thermal Insulation Blanket.

.6	CAN/CGSB-51.12-95	Thermal Insulating and Finishing Cement

.7	CAN/CGSB-51.40-95	Flexible, Elastomeric, Unicellular Thermal Insulation, Sheet and Pipe Covering

.8	CAN/CGSB-51.53-95	Poly(Vinyl Chloride) Jacketing Sheet, for Insulated Pipes, Vessels and Round Ducts

.9	CAN/ULC-S102-1988	Surface Burning Characteristics of Building Materials and Assemblies

.10	CGSB 51-GP-52Ma	Vapour Barrier Jacket and Facing Material of Pipe, Duct and Equipment Thermal Insulation

.11	NFPA 255-1996	Method of Test of Surface Burning Characteristics of Building Materials

END OF DATA SHEET

1.	General

1.1	RELATED REQUIREMENTS

.1	Mechanical General Requirements:	Section 20 00 13.

1.2	PRODUCT OPTIONS AND SUBSTITUTIONS

.1	Refer to Division 01 for requirements pertaining to product options and substitutions.

1.3	SHOP DRAWINGS AND PRODUCT DATA

.1	Comply with requirements of Section 20 00 13.

.2	Submit an insulation schedule, for each application include the following information:

.1	Materials

.2	"k" value

.3	Thickness

.4	Density

.5	Finish

.6	Jacketing

.3	Submit product data and test reports when requested to substantiate that insulation and recovery assemblies meet flame/smoke development ratings and performance requirements for the assembly and thickness used.

1.4	DEFINITIONS

.1	For the purposes of this Section, the following definitions apply:

.1	Concealed:  piping systems and equipment in trenches, shafts, furring, and suspended ceilings.

.2	Exposed:  piping systems and equipment in mechanical rooms or otherwise not "concealed".

.3	"k" Value:  thermal conductivity of insulating material per unit of thickness (W/m.oC).

1.5	FLAME/SMOKE DEVELOPMENT RATINGS

.1	Pipe insulations, recovery materials, tapes, vapour barrier facings and adhesives shall have maximum flame spread rating of 25 and maximum smoke developed rating of 100 except in plenum spaces and air handling systems where maximum smoke development rating shall be 50, when tested in accordance with CAN/ULC-S102-1998, NFPA 255-1996, or ASTM E84-96a.

.2	Insulating materials and accessories shall withstand service temperatures without smoldering, glowing, smoking or flaming when tested in accordance with ASTM C411-82.

2.	Products

2.1	HOT PIPE INSULATION

.1	Hot Pipe Insulation - Mineral Fibre

.1	Material:  formed rigid mineral fibre insulation sleeving to CAN/CGSB-51.9-92.

.2	"k" Value:  maximum 0.035 W/m.oC at 24oC mean temperature.

.3	Service Temperature:  up to 150oC.

.4	Jacket:  factory applied general purpose jacket.

.2	Hot Pipe Insulation - Black Rubber

.1	Material:  flexible elastomeric unicellular preformed pipe covering to CAN/CGSB-51.40-95.

.2	"k" Value:  0.04 W/m. oC at 24oC mean temperature.

.3	Service Temperature:  up to 100oC.

.4	Maximum Allowable Thickness:  25 mm.

2.2	HOT EQUIPMENT INSULATION

.1	Hot Equipment Insulation - Flat Surfaces

.1	Material:  rigid mineral fibre to CAN/CGSB-51.10-92.

.2	"k" Value:  maximum 0.035 W/m.oC at 24oC mean temperature.

.3	Service Temperature:  20oC to 120oC.

.2	Hot Equipment Insulation - Curved Surfaces:

.1	Material:  mineral fibre blanket to CAN/CGSB 51.11-92.

.2	"k" Value:  maximum 0.035 W/m.oC at 24oC mean temperature.

.3	Service Temperature:  20oC to 120oC.

2.3	COLD PIPE INSULATION

.1	Cold Pipe Insulation:  Mineral Fibre.

.1	Material:  formed mineral fibre rigid insulation sleeving to CAN/CGSB 51.9-92.

.2	"k" Value:  maximum 0.035 W/m.oC at 24oC mean temperature.

.3	Service Temperature:  -14oC to 100oC.

.4	Jacket:  factory applied vapour barrier jacket to CGSB 51-GP-52Ma, Type 1, with longitudinal lap seal.

.2	Cold Pipe Insulation - Black Rubber

.1	Material:  flexible elastomeric unicellular preformed pipe covering to CAN/CGSB-51.40-95.

.2	"k" Value:  0.04 W/m. oC at 24oC mean temperature.

.3	Service Temperature:  -4oC to 100oC.

.4	Maximum Allowable Thickness:  25 mm.

2.4	COLD EQUIPMENT INSULATION

.1	Cold Equipment Insulation - Flat Surfaces:

.1	Materials:  rigid mineral fibre to CAN/CGSB-51.10-92.

.2	"k" Value:  maximum 0.035 W/m.oC at 24oC mean temperature.

.3	Service Temperature:  -14oC to 100oC.

.4	Jacket:  factory applied vapour barrier jacket to CGSB-51-GP-52Ma, Type 1.

.2	Cold Equipment Insulation - Curved Surfaces:

.1	Material:  mineral fibre blanket to CAN/CGSB-51.11-92.

.2	"k" Value:  maximum 0.035 W/m.oC at 24oC mean temperature.

.3	Service Temperature:  -14oC to 100oC.

.4	Jacket:  factory applied vapour barrier jacket to CGSB 51-GP-52Ma, Type 1.

2.5	ACCESSORIES

.1	For mineral fibre insulation materials:

.1	Joint Tape:  100 mm wide tape with vapour barrier, fixed in place with manually applied adhesive.

.2	Adhesive:  quick setting adhesive for joints and lap sealing.

.2	Black Rubber Insulation Adhesive:  manufacturers recommended contact cement.

.3	Finishing Cement:  to CAN/CGSB-51.12-95, Type 1 - mineral fibre hydraulic setting thermal insulating and finishing cement for use up to 650oC.

2.6	RECOVERY MATERIALS

.1	Canvas:  ULC listed, 220 g/m2  plain weave cotton fabric.

.2	Aluminum:  0.5 mm thick with longitudinal slip joints and 50 mm end laps, 0.4 mm thick die shaped fitting covers with factory attached protective liner on interior surface.

.3	PVC:  to CAN/CGSB-51.33-M89, [0.38] [    ] mm thick for interior use [and [    ] mm thick for exterior use], off-white in colour with one-piece premoulded fitting covers.

.4	Black Rubber Finish:  insulation manufacturers recommended vinyl lacquer type coating.

3.	Execution

3.1	INSTALLATION, GENERAL

.1	Apply insulation after required piping system tests have been completed and inspected by the Minister.

.2	Ensure insulation is continuous through walls and floor penetrations.

.3	Ensure piping surface is clean and dry before insulating.

.4	Locate cover seams in least visible locations.

.5	Stagger butt joints where multi-layered insulation is used.

.6	On vertical piping with diameters 25 mm and larger, use insulation supports welded or bolted to pipe directly above lowest pipe fitting.  Repeat supports on 4.5 m centers and at each valve and flange.

.7	Tightly fit insulation sections to pipe to make smooth and even surfaces.  Cut insulation for proper fit where weld beads protrude.  Bevel away from studs and nuts to allow their removal without damage to insulation.  Trim closely and neatly around extending parts of pipe saddles, supports, hangers, clamp guides and seal with insulating/finishing cement.

3.2	HOT PIPE INSULATION APPLICATION

.1	Apply mineral fibre insulation when pipe surface temperatures are 50oC to 60oC.

.2	Apply mineral fibre insulation and recovery over full length of pipe without penetration of hangers, interruption at sleeves and fittings.  Apply adhesive to ends of butt joints and seal joint seams with 100 mm wide strips of joint tape.

.3	Terminate mineral fibre insulation at each end of unions and flanges.  Trowel finishing cement into bevel.

.4	Cover fittings and valves with equivalent thickness of finishing cement.  Apply finishing cement over exposed fittings and valves before applying canvas recovering.

.5	Cut mineral fibre insulation layers straight on 10 m centers with 25 mm gap to allow for expansion between terminations.  Pack void tightly with insulation and protect joints with aluminum sleeves.

.6	Seal black rubber insulation butt joints and seams with black rubber insulation adhesive.

.7	Recover exposed mineral fibre insulated piping with [canvas] [PVC] [aluminum].

.8	Recover mineral fibre insulated piping exposed to outdoors with aluminum.

.9	Coat exposed black rubber insulation with two coats of black rubber finish material.

.10	Do not insulate the following piping system components:

.1	Hot water heating piping in radiation cabinets.

.2	Unions, flanges, strainers, expansion joints, flexible piping connectors.

.3	Condensate trap assemblies and drip legs.

.4	Chrome plated or stainless steel piping.

.5	Valve bonnets on domestic water systems.

3.3	HOT EQUIPMENT INSULATION APPLICATION

.1	Use rigid fibreboard for flat surfaces and blanket for curved surfaces.

.2	Tightly butt edges and stagger joints.  Weld mechanical fastener pins to equipment where necessary.

.3	Cover insulation with 25 mm galvanized hexagonal mesh and 12 mm coat of insulating cement.  Finish with a final 12 mm coat of finishing cement and recover with canvas.

3.4	COLD PIPE INSULATION APPLICATION

.1	Insulate 2 m portion of plumbing vents measured from roof outlet back.  Do not insulate remaining vent piping.

.2	Insulate storm sewer piping throughout.  Insulate final 2 m portion from outlet drain back with 25 mm insulation.

.3	Apply mineral fibre insulation and recovery over full length of pipe without penetration of hangers, interruption at sleeves and fittings.  Apply adhesive to ends of butt joints and seal joint seams with 100 mm wide strips of joint tape.

.4	Insulate complete system including valves, unions, flanges, strainers.  Cover fittings and valves with equivalent thickness of finishing cement.  Cover finishing cement with open mesh glass cloth and adhesive.  Seal lap joints with 100% coverage of joint tape and seal the assembly with adhesive.

.5	Seal black rubber insulation butt joints and seams with black rubber insulation adhesive.

.6	Recover exposed mineral fibre insulated piping with [canvas] [PVC] [aluminum].

.7	Recover mineral fibre insulated piping exposed to outdoors with [aluminum] [PVC].

.8	Coat exposed black rubber insulation with two coats of black rubber finish material.

3.5	COLD EQUIPMENT INSULATION APPLICATION

.1	Tightly butt edges and stagger joints.  Seal joints with 100 mm wide strips of joint tape.  Seal with adhesive.

.2	Cover insulation with 25 mm galvanized hexagonal mesh and 12 mm coat of finishing cement.  Finish with a final 12 mm coat of finishing cement and recover with canvas.

3.6	INSULATION TYPE AND THICKNESS SCHEDULE

| Service Type and Nominal Pipe Diameter (mm) | Insulation Type | Insulation Thickness (mm) |
| --- | --- | --- |
| Hot water heating |  |  |
| 50 and smaller | Hot pipe | 25 |
| 65 and larger | Hot pipe | 40 |
| Domestic hot water and recirculation |  |  |
| 40 and smaller | Hot pipe | 12 |
| 50 and larger | Hot pipe | 25 |
| Refrigerant |  |  |
| 25 and smaller | Cold pipe | 25 |
| 30 and larger | Cold pipe | 40 |
| Domestic cold water |  |  |
| All sizes | Cold pipe | 12 |
| Plumbing vents |  |  |
| All sizes | Cold pipe | 25 |
| Storm sewer piping, |  |  |
| All sizes | Cold pipe | 12 |
| Final 2 m section | Cold pipe | 25 |
| Heat exchangers | Hot equipment | 50 |
| Hot water storage tanks | Hot equipment | 50 |
| [Water softeners] | Cold equipment | 25 |
| Roof drains | Cold equipment | 25 |

END OF SECTION