Section Cover Page

Section 20 20 40 2010-12-01 Expansion Compensation

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Reference Standard

1.2	Shop Drawings

1.3	General Requirements

1.4	Inspection

2.	Products

2.1	Flexible Pipe Connections

2.2	Expansion Joints

2.3	Connections

3.	Execution

3.1	Application

3.2	Installation

1.	General

1.1	REFERENCE STANDARD

.1	Conform to Standards of "Expansion Joint Manufacturers Association" and manufacturer's recommendations.

1.2	SHOP DRAWINGS

.1	Flexible pipe connector shop drawing data shall include maximum allowable temperature and pressure rating, overall face-to-face length, live length, hose wall thickness, hose convolutions per 300 mm and per assembly, fundamental frequency of assembly, braid structure and total number of wires in braid.

.2	Expansion joint shop drawings shall include maximum allowable temperature and pressure rating, and maximum expansion compensation.

1.3	GENERAL REQUIREMENTS

.1	Examine piping layout and notify the Minister of additional anchors or expansion joints required to adequately protect system.

.2	Base expansion calculation on 10°C installation temperature to 100°C for hot water heating and 60°C for domestic hot water, plus 30% safety factory.

1.4	INSPECTION

.1	Provide inspection services by flexible pipe manufacturer's representative for final installing and certify installation is in accordance with manufacturer's recommendations and connectors are performing satisfactorily.

2.	Products

2.1	FLEXIBLE PIPE CONNECTIONS

.1	For steel piping construct with stainless steel inner hose and braided exterior sleeve.

.2	For copper piping construct with bronze inner hose and braided exterior sleeve.

.3	Use connectors suitable for minimum 860 kPa WSP and 230°C and 1380 kPa WOG and 120°C.

.4	Construct spool pieces to exact size for insertion of flexible connection.

2.2	EXPANSION JOINTS

.1	Steel piping 75 mm and under:  stainless steel bellows type with antitorque device, limit stops and internal guide.

.2	Steel piping over 75 mm:  external ring controlled type with hydraulically formed stainless steel bellows.

.3	Steel piping 50 mm and over:  spool type expansion, flexible compensator with tapped steel flanges, [teflon] [neoprene and nylon] body suitable for minimum [     ]kPa working pressure and [    ]°C.

.4	Copper piping:  all bronze type with two-ply bronze bellows, anti-torque device limit stops, internal guides and solder joint end.

.5	Use joints suitable for minimum 860 kPa WSP and 200°C, and 1380 kPa WOG and 120°C.

.6	Copper or steel piping 50 mm and under:  low pressure compensators with two-ply bronze bellows suitable for minimum 520 kPa pressure and 120°C, and maximum 12 mm expansion.

.7	Copper or steel piping 50 mm and under:  copper type with packed sliding sleeve suitable for minimum 860 kPa working pressure and 120°C.

2.3	CONNECTIONS

.1	Provide [flexible pipe connectors] [and expansion joints] suitable to connect to adjoining piping as specified for pipe joints.  Use pipe sized units.

3.	Execution

3.1	APPLICATION

.1	Provide flexible pipe connectors on pipes connected to equipment supported by vibration isolation where indicated on the drawing.

.2	Provide structural work and equipment required to control expansion and contraction of piping, loops, pipe offsets, and swing joints and provide corrugated bellows type expansion joints where indicated or required.

3.2	INSTALLATION

.1	Install flexible connectors at right angles to displacement.  Install one end immediately adjacent to isolated equipment and anchor other end.

.2	Rigidly anchor pipe to building structure at points shown, and where necessary provide pipe guides so that movement takes place along axis of pipe only.

END OF SECTION