Section Cover Page

Section 20 40 35 2008-05-01 Hot Water Specialties

This Master Specification Section contains:

.1	This Cover Page

.2	Specification Section Text:

1.	General

1.1	Quality Assurance

2.	Products

2.1	Vents

2.2	Air Separators

2.3	Valves

2.4	Strainers

2.5	Combination Pump Inlet and Strainer Fitting

3.	Execution

3.1	Vents

3.2	Air Separators

3.3	Valves

1.	General

1.1	QUALITY ASSURANCE

.1	Comply with Provincial Regulations and have products CSA approved.

.2	Submit shop drawings and schedules for review when requested.

2.	Products

2.1	VENTS

.1	Manual Air Vents:  short vertical section of 50 mm dia. pipe to form air chamber with 3 mm brass needle valve at top of chamber.

.2	Automatic Float Vent:  vent with isolating valve, brass or semi-steel body, copper float, stainless steel valve and valve seat, suitable for system operating temperature and pressure.

2.2	AIR SEPARATORS

.1	Provide centrifugal type with 860 kPa steel tank, galvanized steel 5 mm perforated strainer, perforated stainless steel air collector tube and drain connection.

2.3	VALVES

.1	Relief Valves:  direct spring loaded type, lever operated, non-adjustable factory set, discharge pressure, ASME rated.

.2	Combination Check and Shut-Off Valve:  angle or straight type with screwed or flanged cast iron body, and bronze disc and seat.

.3	Handwheel Radiator Valves:  angle or straight rising stem globe valve, with bronze body and renewable composition disc.

.4	Radiator Balancing Valves:  angle or straight rising stem, combination, balancing, indicating and shut-off valve.  Body, bonnet, stem and packing nut of bronze or brass with stainless steel dial plate and lockable yoke.

.5	Pressure Reducing Valve, Boiler Feed:  adjustable pressure reducing valve, bronze body construction, corrosion resistant disc and seat, removable stainless steel strainer, rated for 860 kPa working pressure.

2.4	STRAINERS

.1	Bronze or iron body construction, screw or flanged connection, "Y" pattern with removable 1.27 mm stainless steel perforated screen.

2.5	COMBINATION PUMP INLET AND STRAINER FITTING

.1	Provide angle type suction guide fitting with flanged cast iron body, steel or cast iron guide vanes and removable stainless steel strainer.

3.	Execution

3.1	VENTS

.1	Install manual type at system high points.

.2	Install automatic float type at heating units and system high points not readily accessible for servicing, provide vent tubing to nearest drain.

.3	Install automatic washer type for convection type heating units.

3.2	AIR SEPARATORS

.1	Provide air separator on suction side of system circulation pump and connect to expansion tank.

3.3	VALVES

.1	Provide relief valves on pressure tanks, low pressure side of reducing valves, heating convertors, expansion tanks and where indicated.

.2	Drain relief valve to nearest floor drain.

.3	Install on water inlet to terminal heating units such as radiation, unit heaters and fan coil units.

.4	Install on water outlet from terminal heating units.

.5	Install upstream of pressure reducing valve and bypass arrangement.

END OF SECTION