Section Cover Page

Section 20 40 40 2008-05-01 Refrigeration Specialties

This Master Specification Section contains:

.1	This Cover Page

.2	Specification Section Text:

1.	General

1.1	Regulatory Requirements

2.	Products

2.1	Liquid Indicators

2.2	Strainers and Driers

2.3	Valves

2.4	Connectors

3.	Execution

3.1	Liquid Indicators

3.2	Strainers and Driers

3.3	Solenoid Valves

3.4	Expansion Valves

3.5	Charging Valves

3.6	Flexible Connectors

1.	General

1.1	REGULATORY REQUIREMENTS

.1	Comply with Provincial Regulations and Mechanical Refrigeration Codes.

2.	Products

2.1	LIQUID INDICATORS

.1	Type:  double port with liquid indicators, copper brass body, and flared or solder ends.

.2	Seal:  removable seal caps on each port to inspect refrigerant condition.

2.2	STRAINERS AND DRIERS

.1	Strainers:  angle replaceable, cartridge with brass shell.

.2	Refrigerant Driers:  copper or brass shell with replaceable desiccant drier material.

.3	Combination Filter-driers:  replaceable desiccant drier material.

2.3	VALVES

.1	Solenoid Valves, as follows:

.1	Stem:  manually operated acting as a bypass during coil failure.

.2	Coil Assembly:  replaceable.

.2	Expansion Valves, internal of external equalizer, adjustable superheat setting, and as follows:

.1	Body:  brass.

.2	Accessories:  capillary tube and remote sensing bulb.

.3	Charging Valves:  with removable core and quick coupling inlet connection.

2.4	CONNECTORS

.1	Flexible Connectors, as follows:

.1	Type:  close pitch corrugated.

.2	Body:   bronze hose with single layer exterior braiding.

.3	Length:  minimum 230 mm long.

3.	Execution

3.1	LIQUID INDICATORS

.1	Provide full size in main liquid line leaving condenser. If a receiver is used, install in liquid line leaving receiver.

3.2	STRAINERS AND DRIERS

.1	Provide full size strainer ahead of each automatic valve. Where multiple expansion valves with integral strainers are used, install single main liquid line strainer.

.2	Provide shut-off valve on each side of strainer to facilitate maintenance.

.3	Provide full flow permanent refrigerant drier in low temperature systems and systems utilizing hermetic compressors.

.4	Mount drier vertically in liquid line adjacent to receiver with three valve bypass assembly to permit isolation of drier for servicing.

.5	Install filter-driers with three valve bypass assembly to permit isolation for servicing.

3.3	SOLENOID VALVES

.1	Provide solenoid valves in liquid line of systems operating with single pump-out or pump-down compressor control, in liquid line of single or multiple evaporator systems and in oil bleeder lines from flooded evaporators to stop flow of oil and refrigerant into the suction line when system shuts down.

3.4	EXPANSION VALVES

.1	Size expansion valves properly to avoid penalty of being undersized at full load and of being excessively oversized at partial load.

.2	Properly evaluate refrigerant pressure drop through system to determine the available pressure drop across the valve.

.3	Select valves for maximum load at design operating pressure and minimum 42°C of superheat.

.4	Locate remote expansion valve sensing bulb immediately after evaporator outlet and suction line.

3.5	CHARGING VALVES

.1	Provide refrigerant charging connections in liquid line between receiver shut-off valve and expansion valve.

3.6	FLEXIBLE CONNECTORS

.1	Use flexible connectors only at or near compressors.

END OF SECTION