Section Cover Page

Section 22 13 65 2010-12-01 Sewage Holding Tanks

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if project: .1 is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

Use this Section to specify requirements which apply specifically to holding tanks.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Related Sections

1.2	Unit Prices

1.3	Reference Documents

2.	Products

2.1	Pipe

2.2	Sewage Holding Tanks

2.3	Alarm System

2.4	Bedding and Backfill Material for Fiberglass Tanks

3.	Execution

3.1	Excavation

3.2	Sewage Holding Tank Installation

3.3	Alarm System Installation

LEED Notes:

Refer to Section 01 35 18 – LEED Requirements for:

1.	Requirements necessary for this project to obtain points required for certification.

2.	Confirmation of LEED prerequisites and credits affecting this Section; not all are mandatory for certification

Maintain built-in sustainability regardless of LEED requirements for:

.1	Recycling, reuse of materials, components and assemblies.

.2	Diversion of construction waste from landfills.

.3	Use of recycled materials, local materials, rapidly renewable and durable materials.

.4	Maintain healthy indoor environment during constructing.

.5	Provide for thermal comfort, access to views and daylight for indoor spaces.

.6	Foster innovation into facility design and planning.

LEED Credits:

Water Efficiency

Credit 2 – Innovative Wastewater Technologies

.1	Requirements:  Reduce the use of municipally provided potable water for building sewage conveyance by a minimum of 50%. OR Treat 50% of wastewater on site to tertiary standards.

.2	Strategies:  Collect grey-water from sinks, showers and other sources. The collected grey-water can then be used for flushing toilets, landscaping, and other functions thus reducing the demand on municipally provided potable water.

-	Rainwater capture can offset the use of municipally provided potable water for flushing toilets, landscaping, and other functions.

-	Consider an on-site wastewater treatment systems such as constructed wetlands, a mechanical recirculating sand filter, or an aerobic biological treatment reactor.

1.	General

1.1	RELATED SECTIONS

.1	Fill Materials:	Section 31 05 13.

.2	Earthwork General Requirements:	Section 31 20 10.

.3	Site Excavating, Filling and Grading:	Section 31 23 10.

1.2	UNIT PRICES

SPEC NOTE:  For Unit Price Contracts only.

.1	Payment for holding tank will be on a lump sum basis for a complete supply and installation [including alarms].

1.3	reference Documents

.1	Canadian Standards Association:

| .1 | CAN/CSA-B66-05 | Design, Material, and Manufacturing Requirements for Prefabricated Septic Tanks and Sewage Holding Tanks |
| --- | --- | --- |
| .2 | CSA B181.1-06 | Acrylonitrile-butadiene-styrene (ABS) drain, waste, and vent pipe and pipe fittings (Part of Thermoplastic Nonpressure Piping Compendium CAN/CSA B1800-06) |
| .3 | CSA B181.2-06 | Polyvinylchloride (PVC) and chlorinated polyvinylchloride (CPVC) drain, waste, and vent pipe and pipe fittings (Part of Thermoplastic Nonpressure Piping Compendium CAN/CSA B1800-06) |

2.	Products

2.1	PIPE

.1	ABS-DWV Pipe:  to CSA B181.1, belled ends, solvent joints.

.2	PVC-DWV Pipe:  CSA B181.2, belled ends, solvent joints.

2.2	SEWAGE HOLDING TANKS

.1	To CAN/CSA-B66.

.2	[Reinforced precast concrete] [Fiberglass reinforced plastic]  Holding tank to the following requirements:

.1	Holding Chamber capacity [         ]L.

.2	Manholes:  [two 500 mm diameter manholes] [one 600 mm manhole].

.3	Bury depth:  [           ] mm.

.4	Other dimensions and requirements are shown on drawings.

2.3	ALARM SYSTEM

1	Alarm Unit:  [                         ].

2	Liquid level regulator c/w adequate length of cable and 120/16 V transformer.

2.4	BEDDING AND BACKFILL MATERIAL FOR FIBERGLASS TANKS

.1	[Washed Pea Gravel] [20 mm Crushed Gravel], as specified in Section 31 05 13.

3.	Execution

3.1	EXCAVATION

.1	Form boxed excavation having level bottom and stable vertical sides.

.2	Excavate to 1000 mm maximum clearance around all sides of tank.

3.2	SEWAGE HOLDING TANK INSTALLATION

.1	For concrete tank, place bedding on levelled subgrade to 300 mm compacted depth.  Compact gravel to [95] [   ]% Standard Proctor Maximum Dry Density.

.2	For fiberglass reinforced plastic tank, place bedding material on levelled subgrade to 300 mm compacted depth, and install as per manufacturer's instructions.

.3	Set tank to specified elevation and location on top of compacted base.  Ensure pipe inverts specified can be maintained.

.4	Extend manholes of tank to [surface] [150] [    ] mm below surface.

3.3	ALARM SYSTEM INSTALLATION

.1	Install high water alarm system as shown on the drawings.

.2	Locate alarm units [inside buildings] [location to be determined on site].

.3	Connect to [existing electrical panel] [new panel].

.4	Seal conduit at both ends and around at penetration points building and tank.

.5	Conduit may be installed exposed inside the buildings.

.6	Conduit to be 12 mm PVC.

.7	Coordinate alarm unit locations and electrical runs with Minister.

END OF SECTION