Section Cover Page

Section 23 07 00 2015-12-09 Ductwork and Breeching Insulation

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if: .1 project is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

This Master Specification Section contains:

.1	This Cover Sheet

.2	LEED Notes and Credits

.3	Specification Section Text:

1.	General

1.1	Related Requirements

1.2	Reference Documents

1.3	Product Options and Substitutions

1.4	Submittals

1.5	Definitions

1.6	Flame/Smoke Development Ratings

1.7	Delivery, Storage and Handling

1.8	Quality Assurance

2.	Products

2.1	Hot Duct Insulation

2.2	Cold Duct Insulation

2.3	Acoustic Ductwork Insulation

2.4	Breeching Insulation

2.5	Accessories

2.6	Recovery Materials

3.	Execution

3.1	Installation, General

3.2	Hot Duct Insulation Application

3.3	Cold Duct Insulation Application

3.4	Acoustic Duct Insulation Application

3.5	Breeching Insulation Application

3.6	Exposed Ducts

3.7	Insulation Type and Thickness Schedule

LEED Notes:

Refer to Section 01 35 18 – LEED Requirements for:

1.	Requirements necessary for this project to obtain points required for certification.

2.	Confirmation of LEED prerequisites and credits affecting this Section; not all are mandatory for certification

Maintain built-in sustainability regardless of LEED requirements for:

.1	Recycling, reuse of materials, components and assemblies.

.2	Diversion of construction waste from landfills.

.3	Use of recycled materials, local materials, rapidly renewable and durable materials.

.4	Maintain healthy indoor environment during constructing.

.5	Provide for thermal comfort, access to views and daylight for indoor spaces.

.6	Foster innovation into facility design and planning.

LEED Credits:

Energy & Atmosphere

Prerequisite 2 – Minimum Energy Performance

SPEC NOTE:  Though prerequisites do not contribute to a projects point score, they are mandatory and MUST be met for a project to receive LEED Canada – NC certification.

Credit 1 – Optimize Energy Performance

Materials & Resources

Credit 2 – Construction Waste Management

# General

## RELATED REQUIREMENTS

### Mechanical General Requirements:	Section 20 00 13.

## REFERENCE DOCUMENTS

### American Society for Testing and Materials (ASTM):

|  | ASTM B209M | Specification for Aluminum and Aluminum Alloy Sheet and Plate |
| --- | --- | --- |
|  | ASTM C335 | Test Method for Steady State Heat Transfer Properties of Horizontal Pipe Insulation |
|  | ASTM C411 | Standard Test Method for Hot-Surface Performance of High Temperature Thermal Insulation |
|  | ASTM C423 | Standard Test Method for Sound Absorption and Sound Absorption Coefficients by Reverberation Room Method |
|  | ASTM C449 | Standard for Specification for Mineral Fiber Hydraulic–Setting Thermal Insulating and Finishing Cement |
|  | ASTM C553 | Standard Specification for Mineral Fiber Blanket Thermal Insulation for Commercial and Industrial Applications |
|  | ASTM C921 | Practice for Determining the Properties of Jacketing Materials for Thermal Insulation |
|  | ASTM C1071 | Standard Specification for Fibrous Glass Duct Lining Insulation (Thermal and Sound Absorbing Material) |
|  | ASTM G21 | Standard of Practice for Determining Resistance of Synthetic Polymeric Materials to Fungi |

### American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE):

|  | ASHRAE 90.1-2010 | Energy Standard for Buildings Except Low-Rise Residential Buildings |
| --- | --- | --- |

SPEC NOTE: Specify Article 1.2.3 only if this is a LEED project

### Canada Green Building Council (CaGBC):

|  | LEED Canada 2009 Rating System | LEED Canada for New Construction and Major Renovations. LEED Canada for Core and Shell Development. Website: www.cagbc.org |
| --- | --- | --- |

### National Research Council of Canada

#### NECB-2011			National Energy Code of Canada for Buildings

### National Fire Protection Association (NFPA):

|  | NFPA 255 | Standard Method of Test of Surface Burning Characteristics of Building Materials |
| --- | --- | --- |

### Sheet Metal and Air Conditioning Contractor’s National Association (SMACNA)

|  | SMACNA | HVAC Duct Construction Standards - Metal and Flexible |
| --- | --- | --- |

### Thermal Insulation Association of Canada (TIAC)

#### TIAC				Mechanical Insulation Best Practice Guide

### Underwriters Laboratories of Canada (ULC):

|  | CAN/ULC-S102-10 | Standard Method of Test for Surface Burning Characteristics of Building Materials and Assemblies |
| --- | --- | --- |

## PRODUCT OPTIONS AND SUBSTITUTIONS

### Refer to Division 01 for requirements pertaining to product options and substitutions.

## submittals

### Product Data:

#### Submit manufacturer’s product data in accordance with Section 01 33 23 – Shop Drawings, Product Data and Samples.

##### Submit product data and test reports when requested to substantiate that insulation and recovery assemblies meet flame/smoke development ratings and performance requirements for the assembly and thickness used.

### Shop Drawings:

#### Submit shop drawings in accordance with Section 01 33 23 – Shop Drawings, Product Data and Samples.

##### Submit an insulation schedule, for each application include the following information:

###### Materials

###### "k" value

###### Thickness

###### Density

###### Finish

###### Jacketing

### Submit information showing installed insulation thicknesses meet the minimum performance requirements of the National Energy Code of Canada for Buildings 2011 (NECB-2011) or ASHRAE 90.1-2010. The more stringent requirements shall apply.

## DEFINITIONS

### For the purposes of this section, the following definitions apply:

#### Concealed:  ductwork and equipment in shafts, furring, suspended ceilings and attics.

#### Exposed:  ductwork and equipment in mechanical rooms or otherwise not "concealed".

#### "k" Value:  thermal conductivity of insulating material per unit of thickness (W/m.°C) to ASTM C553.

## FLAME/SMOKE DEVELOPMENT RATINGS

### Duct insulation, recovery materials, vapour barrier facings, tapes and adhesives shall have maximum flame spread rating of 25 and maximum smoke developed less than or equal to 50, when tested in accordance with CAN/ULC S102.

### Insulating materials and accessories shall withstand service temperatures without smoldering, glowing, smoking or flaming when tested in accordance with ASTM C411.

## Delivery, Storage, and Handling

### Separate waste materials for [reuse] [and] [recycling] in accordance with Section 01 74 19 – Waste Management and Disposal.

## quality assurance

### Insulation materials shall be new, undamaged and of the respective types specified for each specific application.

### Installer to be specialist in performing work of this section and have at least 3 years successful experience with work of similar complexity and size as required for this project.

### Contractor and tradespeople hold a recognized credential to work as insulator in Alberta, and is a member of TIAC.

### Installation conforms to TIAC Mechanical Insulation Best Practices Guide.

# Products

## HOT DUCT INSULATION

### Hot Duct Insulation - Round and Oval:

#### Material:  flexible mineral fiber blanket insulation to ASTM C553 faced with factory applied vapour retarder jacket.

#### "k" Value:  maximum 0.038 W/m.°C at 24°C mean temperature.

#### Service Temperature:  20°C to 65°C.

### Hot Duct Insulation - Rectangular

#### Material:  rigid mineral fiber insulation to ASTM C612 with factory applied vapour retarder jacket.

#### "k" Value:  maximum 0.035 W/m.°C at 24°C mean temperature.

#### Service Temperature:  20°C to 65°C.

## COLD DUCT INSULATION

### Cold Duct Insulation - Round and Oval:

#### Material:  flexible mineral fiber blanket insulation.

#### "k" Value:  maximum 0.038 W/m.°C at 24°C mean temperature.

#### Service Temperature:  -40°C to 65°C.

#### Jacket:  factory applied reinforced aluminum foil vapour barrier.

### Cold Duct Insulation - Round (Exposed to Outdoors):

#### Material:  semi-rigid mineral fiber in roll form.

#### "k" Value:  maximum 0.038 W/m.°C at 24°C mean temperature

#### Service Temperature:  -40°C to 65°C.

#### Jacket:  factory applied reinforced aluminum for vapour barrier.

### Cold Duct Insulation - Rectangular:

#### Material:  rigid mineral fiber insulation .

#### "k" Value:  maximum 0.038 W/m.°C at 24°C mean temperature.

#### Service Temperature:  20°C to 65°C.

#### Jacket:  factory applied reinforced aluminum foil vapour barrier.

## ACOUSTIC DUCTWORK INSULATION

### Material:  rigid mineral fiber acoustical insulation to ASTM C1071, Type 2.

### Density:  48 kg/m3 (minimum).

### Acoustic Properties:  minimum NRC of 0.70 for 25 mm thickness based on Type A mounting to ASTM C423.

### "k" Value:  maximum 0.035 W/m°C at 24°C mean temperature when tested in accordance with ASTM C177.

### Service Temperature:  -40°C to 65°C.

### Surface Finish:  air stream side coated to prevent fibre erosion with surface roughness not exceeding 0.58 mm.

## BREECHING INSULATION

#### Material:  Semi-rigid mineral fiber with glass mat.

#### "k" Value:  Maximum 0.038 W/m°C at 24°C mean temperature.

#### Service Temperature:  65°C to 450°C.

## ACCESSORIES

### FSK Tape: vapour barrier tape consisting of laminated aluminum foil, glass fiber scrim and paper, with pressure sensitive self adhesive.

### ASJ Tape: vapour resistant tape consisting of all service jacket material with pressure sensitive self adhesive.

### Contact Adhesive:  quick setting, adhesive to adhere flexible or rigid mineral fibre insulation to ducts.

### Lap Seal Adhesive:  quick setting adhesive for joints and lap sealing of vapour barriers.

### Canvas Adhesive:  dilute, washable, fire retardant lagging adhesive for cementing canvas jacket to duct insulation.

### Pins:  welding pins 4 mm diameter shaft with 35 mm diameter head for installation through the insulation.  Length to suit thickness of insulation with 32 mm square nylon retaining clips.

### Insulating Cement:  hydraulic setting type for use on mineral fiber, meeting requirements of ASTM C449.

## RECOVERY MATERIALS

### Canvas:  ULC listed, 220 g/m2 plain weave cotton fabric treated with fire retardant lagging adhesive to ASTM C921.

### Aluminum Jacket:  ASTM B209, 0.5 mm thick [smooth] [stucco embossed] [corrugated] with aluminum alloy butt straps and vapour barrier secured with mechanical fastener.

# Execution

## INSTALLATION, GENERAL

### Ductwork dimensions shown on drawings are clear inside free area measurement regardless of insulation placement or thickness.  Fabricate ducts accordingly.

### Apply insulation after required duct system tests have been completed and inspected by the Province.

### Ensure duct surfaces are clean and dry before installing insulation.

### Install in accordance with TIAC Mechanical Insulation Best Practices Guide.

### Install in accordance with manufacturers recommendations.

### Install insulation over entire surface of duct, for full length of duct run including portions of duct passing penetrations through walls and floors.

### Install insulation in a manner to insure hangers and standing duct seams do not penetrate insulation.

### Locate finished seams in least visible location.

### Do not insulate ductwork with external thermal insulation where acoustic duct insulation has been specified.

### Install insulation at ambient temperatures within acceptable temperature ratings for tapes, sealants and adhesives.

## HOT DUCT INSULATION APPLICATION

### Adhere insulation to round and oval ductwork with contact adhesive applied in 150 mm wide strips on 400 mm centres.  Band on outside with wire to set adhesive.

### Butt insulation and seal joints with lap seal adhesive; cover joint ASJ tape.

### Secure rigid insulation on rectangular ducts with 50% area coverage using contact adhesive, impale on pins located 400 mm on centre, secure in place with retaining clips.

### Butt rigid insulation on rectangular ducts and seal joints with lap seal adhesive; cover joints with 100 mm strips of open mesh cloth imbedded between two coats of lap seal adhesive.

## COLD DUCT INSULATION APPLICATION

### Adhere mineral fibre insulation to round and oval ductwork with adhesive applied in 150 mm wide strips on 400 mm centres.  Band on outside and remove bands when mastic sets.

### Butt mineral fibre insulation and seal joints with lap seal adhesive; cover joint with FSK tape.

### Secure rigid insulation on rectangular ducts with 50% area coverage of adhesive and impale on pins located 400 mm on centre and secure in place with the retaining clips.

### Butt rigid insulation on rectangular ducts and seal joints with lap seal adhesive; cover joints with 100 mm strips of open mesh cloth imbedded between two coats of lap seal adhesive.

## ACOUSTIC DUCT INSULATION APPLICATION

### Do work in accordance with recommendations of SMACNA duct liner standards as indicated in SMACNA HVAC Duct Construction Standards, Metal and Flexible, except as specified otherwise.

### Install in accordance with manufacturer’s recommendations, and as follows:

#### Fasten to interior sheet metal surface with 100% coverage of adhesive.

#### In addition to adhesive, install weld pins not less than 2 rows per surface and not more than 425 mm on centres.

### Seal butt joints, exposed edges, weld pin and clip penetrations and damaged areas of liner with joint tape and sealer. Install joint tape in accordance with manufacturer’s written recommendations, and as follows:

#### Bed tape in sealer.

#### Apply two coats of sealer over tape.

### Replace damaged areas of liner at discretion of the Province.

### Protect leading and trailing edges of duct sections with sheet metal nosing having 15 mm overlap and fastened to duct.

SPEC NOTE: Provide protective film and perforated metal liner on acoustic lined ductwork in hospital/healthcare facilities (Reference CSA Z317.2).

## BREECHING INSULATION APPLICATION

### Face breeching with 10 mm rib lath turn out to provide 13 mm space between insulation and hot surface and 13 mm mesh expanded lath on the outside.

### Butt insulation firmly together and secure with 1.6 mm galvanized wire.

### Lace metal mesh together.

### Coat with 13 mm thick insulating cement.

### Finish with a final 13 mm coat of insulating.  Trowel to a smooth hard finish.

### Recover with aluminum jacket.

## EXPOSED DUCTS

### Provide recovery jackets on indoor exposed insulation throughout including equipment rooms:

#### Mechanical rooms: [canvas] [aluminum].

#### Occupied spaces: aluminum.

#### Equipment rooms: [canvas] [aluminum].

### Cover insulation exposed to outdoors throughout with aluminum jacket secured with aluminum bands on 200mm centres.  Seal all joints on jacket for weathertight finish with compatible water proof lap cement.  Locate longitudinal joints in least weather exposed position.

## INSULATION TYPE AND THICKNESS SCHEDULE

| Service Type | Insulation Type | Insulation Thickness (mm) |
| --- | --- | --- |
| Exhaust and relief ducts within 3 m of exterior openings | Hot duct | 50 |
| Relief ducts and plenums | Hot duct | 25 |
| Supply ducts and plenums | Hot duct | 25 |
| [ ] | Hot duct | [ ] |
| Combustion air | Cold duct | 50 |
| Outside air | Cold duct | 100 |
| Mixing plenums | Cold duct | 50 |
| Supply air plenums | Cold duct | 25 |
| Medium pressure supply ducts | Cold duct | 25 |
| Low pressure supply ducts | Cold duct | 25 |
| Supply and return ducts exposed to outdoors | Cold duct | 100 |
| Supply and return ducts in cold attic spaces | Cold duct | 100 |
| Ventilation equipment | Cold duct | 50 |
| Evaporative condenser intake and exhaust | Cold duct | 25 |
| [ ] | Cold duct | [ ] |
| High and Medium pressure supply ducts | Acoustic | 25 |
| Low pressure supply and return | Acoustic | 25 |
| Plenums | Acoustic | 25 |
| [ ] | Acoustic | [ ] |
| Boilers | Breeching | 50 |
| Domestic hot water heaters, atmospheric burners | Breeching | 25 |
| Domestic hot water heaters, forced air burners | Breeching | 50 |
| Furnaces | Breeching | 25 |
| Gas-fired unit heaters | Breeching | 25 |
| Indirect gas-fired air handling units, forced air burners | Breeching | 25 |
| Indirect gas-fired air handling units, atmospheric burners | Breeching | 50 |
| [ ] | Breeching | [ ] |

END OF SECTION