Section Cover Page

Section 23 08 13 General Mechanical Starting 2010-12-31 and Testing Requirements

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if project: .1 is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

Use this Section to specify General Mechanical Starting and Testing Requirements for Division 23 (mechanical equipment and systems).  Do not specify these requirements in individual Division 23 technical sections; include cross-references to this Section 23 08 13 only.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Related Requirements

1.2	Minister’s Witnessing of Tests

1.3	Starting and Testing Costs

1.4	Start-Up Reports

1.5	Reports

1.6	Quality Assurance

1.7	Manufacturer’s Recommendations

1.8	Regulatory Requirements

2.	Products

2.1	Testing Instruments and Equipment

3.	Execution

3.1	Use of Instruments Supplied Under Contract

3.2	Inspection

3.3	Compliance with Defined Procedures

3.4	Check Sheets, Field Reports and Data

3.5	Coordination

3.6	Starting and Testing Phases

3.7	Specialty Agencies and Testing Laboratories

LEED Notes:

Refer to Section 01 35 18 – LEED Requirements for:

1.	Requirements necessary for this project to obtain points required for certification.

2.	Confirmation of LEED prerequisites and credits affecting this Section; not all are mandatory for certification

Maintain built-in sustainability regardless of LEED requirements for:

.1	Recycling, reuse of materials, components and assemblies.

.2	Diversion of construction waste from landfills.

.3	Use of recycled materials, local materials, rapidly renewable and durable materials.

.4	Maintain healthy indoor environment during constructing.

.5	Provide for thermal comfort, access to views and daylight for indoor spaces.

.6	Foster innovation into facility design and planning.

LEED Credits:

Energy and Atmosphere

Prerequisite 1 – Fundamental Commissioning of Building Energy Systems

Note:  Though prerequisites do not contribute to a projects point score, they are mandatory and MUST be met for a project to receive LEED Canada – NC certification.

Credit 3 – Enhanced Commissioning

Note: Building commissioning is a quality assurance method that is implemented to verify and ensure that fundamental building elements and systems are designed, installed and calibrated to operate as intended.  Effective commissioning will ensure that staff are properly trained in the maintenance and operation of the building resulting in building longevity.  A properly commissioned building can also result in significant operational cost saving as energy efficiency often increases.

1.	General

1.1	RELATED Requirements

.1	Contractor Start-Up Report Forms:	Division 01.

.2	Mechanical Equipment Starting and Testing:	Section 23 08 23.

.3	Mechanical System Starting and Testing:	Section 23 08 33.

.4	Balancing and Adjusting of Mechanical  Equipment and Systems:	Section 23 08 83.

.5	EMCS Start-up and Testing:	Section 23 08 95.

1.2	MINISTER’S WITNESSING OF TESTS

.1 	Minister may witness selected starting, testing, adjusting, balancing and cleaning procedures.

.2	Advise the Minister in advance that starting, testing, adjusting, balancing or cleaning processes are ready to commence.  Consult with the Minister to determine which procedures he may elect to witness.  Provide advanced notice prior to commencement of each procedure or series of procedures to allow Minister to arrange for witnessing of tests.

1.3	STARTING AND TESTING COSTS

.1	Pay costs associated with starting, testing, adjusting, balancing and cleaning, including supply of instruments, equipment, supplies, and consumable materials.

1.4	START-UP REPORTS

SPEC NOTE:  Include this article when a formal Facility Start-Up process is not used.

.1	Prepare Start-Up report using forms available from the Minister.

.2	Where forms are not available from the Minister for specific systems or equipment, prepare appropriate forms.

.3	Submit Start-Up reports as part of Operation and Maintenance Manual specified in Section 20 01 06.

1.5	REPORTS

SPEC NOTE:  Include this article when a formal Facility Start-Up process is being used.

.1	Submit Contractor Start-Up Report forms in accordance with Section 01 33 35 documenting starting and testing procedures performed, and observed tests results obtained.

.2	Submit field reports in accordance with Section 23 01 05.

1.6	QUALITY ASSURANCE

.1	Use personnel for starting, testing, adjusting and balancing procedures who have experience in mechanical equipment and systems commissioning, and are able to interpret results of readings and tests and report state of systems in a clear and concise manner.

1.7	MANUFACTURER’S RECOMMENDATIONS

.1	Prior to starting equipment or systems, obtain and review manufacturer's installation, starting and operating instructions. Read in conjunction with procedures specified herein.

.2	Use manufacturer's and supplier's trained personnel where necessary to maintain validity of manufacturer's warranty.

.3	Compare actual installation with manufacturer's recommended installation.  Record discrepancies. Correct deviations detrimental to equipment performance prior to starting equipment.

1.8	REGULATORY REQUIREMENTS

.1	To facilitate expedient turnover of facility at Interim Acceptance of the Work, arrange for regulatory authorities to witness those specified starting procedures that duplicate tests required by regulatory authorities.

.2	Obtain certificates of approval and for compliance with regulations from authorities having jurisdiction. Include copies of certificates with start-up reports.

2.	Products

2.1	TESTING INSTRUMENTS AND EQUIPMENT

.1	Provide testing instruments and equipment and ancillary equipment such as two-way radios and ladders required to perform starting, testing, adjusting and balancing of mechanical equipment and systems.

.2	Submit a list of testing instruments and equipment proposed for use to the Minister for approval.

.3	Use instruments supplied or calibrated by approved laboratory or manufacturer.  Show the Minister original calibration certificate for each instrument to be used. Include copy of calibration certificates with test reports.

.4	Recalibrate instruments at frequency recommended by instrument manufacturer or, in absence of manufacturer’s recommendations, as required by Associated Air Balance Council (AABC).

.5	Use testing instruments and equipment which meet following accuracy requirements:

| Device | Range | Accuracy |
| --- | --- | --- |
| Air Temperature | -40 to 75°C | ±0.l0°C |
| Hydronic temperature | -40 to l20°C | ±0.l0°C |
| Stack Temperature | -40 to 300°C | ±1.00°C |
| Air Velocity Pressure | 0 to 250 Pa | ±2% of reading |
| Air Pressure | 0 to 2500 Pa | ±12.5 Pa |
| Hydraulic Pressure | 0 to 1400 KPa | ±2% of gauge |
| Air Velocity | 0.1 to 20 m/s | ±2% of gauge |
| Sound Meter | 35 to 130 dB | ANSI S 1.4 Type 2 |
| Octave Band Filters | 63 to 8000 Hz | ANSI S 1.11 |
|  |  | Class II |
| Humidity | 10 to 90% RH | ±3.0% |

.6	Following testing instruments and equipment makes and models are also acceptable:

| Equipment | Make | Model |
| --- | --- | --- |
| Sound Level Meter | Quest | 2700 |
| Octave Band Filters | Quest | OB-50 |
| Flue Gas Analyzer | Kane May | KM 9002 |
| Stack Thermometer | Bacharach | 12-7018 |
| Tachometer (contact) | Ono-Sokki | HT-331 |
| Tachometer (strobe) | Ono-Sokki | HT 441 |
| Ammeter | Amprobe | ACD-2 |
| CO Detector | G.C.Industries | GC 401 |
| Sling Psychrometer | Bacharach | 12-7018 |
| Digital Humidity | Vaisala | HM 131 with |
| Sensor |  | HMP 31UT probe |
| Belt Tension Tester | Woods |  |
| Inclined Manometer | Dwyer | 400-10 |
| Air Pressure Gauge | Magnahelic |  |
|  | -125 to 125 Pa | 2300-250 Pa |
|  | 0 to 250 Pa | 2000-250 Pa |
|  | 0 to 1000 Pa | 2000-1 KPa |
|  | 0 to 1500 Pa | 2000-1.5 KPa |
| Fluid Pressure Gauge | Marsh | 0 to 60 psi |
|  | Marsh | 0 to 160 psi |
|  | Marsh | 30"Hg - 60 psi |
| Thermometer | Palmer | MS-13 |
| Digital Thermometer | Fluke Multi- | 8062A with |
|  | meter | 80T-150 surface |
|  |  | probe |
|  |  | 80PK-5 piercing |
|  |  | probe |
| Digital Anemometer | ITM Instruments | DA 4000 |
| Micromanometer | Shortridge | 8420 |
| Flow Hood | Shortridge | 8400 with 8420 |
|  |  | meter |
| Air Quality Monitor | Armstrong | AMC-l0l3P |

3.	Execution

3.1	USE OF INSTRUMENTS SUPPLIED UNDER CONTRACT

.1	Instruments for testing, adjusting and balancing supplied under this contract may be used provided the Minister is satisfied that instrument accuracy complies with requirements specified above and calibration certificate has been provided with each instrument.

.2	Use “Calibrated Air Flow Measuring Stations” to measure air flow during system balancing and coil performance testing.

.3	Use balancing valve pressure tappings, orifice plates, pitot tube fittings, etc. to measure fluid flow rates.

.4	Calibrated EMCS temperature, humidity and pressure sensors may be used to gather Contractor Start-up Program system performance data provided the Minister confirms that EMCS sensor calibrations have been completed and approved.

3.2	INSPECTION

.1 	Do not conceal or cover equipment or systems until inspected, tested and approved by Minister.

3.3	COMPLIANCE WITH DEFINED PROCEDURES

.1	Failure to follow specified instructions pertaining to correct starting procedures may result in re-evaluation of equipment by independent testing agency selected by the Minister at Contractor's expense.  Should results reveal equipment has not been started in accordance with specified requirements, equipment may be rejected. If rejected, remove equipment from site and replace. Replacement equipment will also be subject to full starting procedures, using same procedures specified for originally installed equipment.

3.4	CHECK SHEETS, FIELD REPORTS AND DATA

.1	Record all data gathered on site on start-up report forms.

.2	Make copies of all starting and testing data before equipment and system start-up personnel leave site.  Maintain one copy of all data taken during starting on site.

.3	Maintain one copy of all final starting, testing, adjusting and balancing reports on site up to Interim Acceptance of the Work for reference purposes.

3.5	COORDINATION

.1	Prior to commencement of each particular testing procedure, coordinate all sub-trades, manufacturers, suppliers and other specialties to ensure all phases of work are properly completed.  Establish necessary manpower requirements.

3.6	STARTING AND TESTING PHASES

.1	Starting and testing program generally consists of following five distinct phases:

.1	Pre-Starting: visual inspection

.2	Starting: actual starting procedure.

.3	Post-Starting: operational testing, adjusting or balancing and equipment run-in phase.

.4	Pre-Interim Acceptance of the Work: final cleaning, re-testing, balancing and adjusting and maintenance.

.5	Post-Interim Acceptance of the Work: retesting and fine-tuning of system to prove all deficiencies have been corrected.

.2	After each distinct phase of work has been completed, correct deficiencies before  commencing the next phase.

3.7	SPECIALTY AGENCIES AND TESTING LABORATORIES

.1	Arrange for reports prepared by special testing agencies and testing laboratories to be submitted directly to the Minister.  Include a copy of each report in Contractor Start-Up Program report.

.2 	Agencies and testing laboratories shall have facilities and qualifications acceptable to the Minister.

END OF SECTION