Section Cover Page

Section 23 08 23 Mechanical Equipment 2010-12-31 Starting and Testing

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if project: .1 is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

Use this Section to specify all Mechanical Equipment Starting and Testing Requirements for Division 23.  Do not specify these requirements in individual Division 23 technical sections; include cross-references to this Section 23 08 23 only.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Intent

1.2	Related Requirements

1.3	Factory Trained Representatives

2.	Products

Not Used

3.	Execution

3.1	Fuel Fired Equipment - Boilers

3.2	Fuel Fired Equipment - Service Water Heaters

3.3	Fuel Fired Equipment - Packaged Direct Fired Air Systems

3.4	Fuel Fired Equipment - Forced Air Furnaces

3.5	Fuel Fired Equipment - Gas Fired Unit Heaters

3.6	Fuel Fired Equipment - Packaged Rooftop Furnace with Cooling

3.7	Fluid Handling Equipment - Pumps

3.8	Fluid Handling Equipment - Heat Exchangers

3.9	Fluid Handling Equipment - Coils

3.10	Fluid Handling Equipment - Electric Steam Grid Humidifier

3.11	Fluid Handling Equipment - Wetted Media Humidifier

3.12	Fluid Handling Equipment - Cooling Towers

3.13	Fluid Handling Equipment - Chillers

3.14	Fluid Handling Equipment - Miscellaneous

3.15	Air Handling Equipment - Air Handling Units

3.16	Air Handling Equipment - Fans

3.17	Air Handling Equipment - Air Flow Measuring Stations

3.18	Air Handling Equipment - VAV Boxes

3.19	Air Handling Equipment - Unit and  Cabinet Heaters

3.20	Air Handling Equipment - Miscellaneous

3.21	Miscellaneous Equipment - Variable Speed Drive Units

3.22	Miscellaneous Equipment - Tanks

3.23	Miscellaneous Equipment - Air Cooled Condensers

3.24	Miscellaneous Equipment - Compressors and Vacuum Pumps

3.25	Miscellaneous Equipment - Packaged Air Conditioning Units

3.26	Miscellaneous Equipment - Fire Extinguishers

3.27	Miscellaneous Equipment - Fire Hose Cabinets

LEED Notes:

Refer to Section 01 35 18 – LEED Requirements for:

1.	Requirements necessary for this project to obtain points required for certification.

2.	Confirmation of LEED prerequisites and credits affecting this Section; not all are mandatory for certification

Maintain built-in sustainability regardless of LEED requirements for:

.1	Recycling, reuse of materials, components and assemblies.

.2	Diversion of construction waste from landfills.

.3	Use of recycled materials, local materials, rapidly renewable and durable materials.

.4	Maintain healthy indoor environment during constructing.

.5	Provide for thermal comfort, access to views and daylight for indoor spaces.

.6	Foster innovation into facility design and planning.

LEED Credits:

Energy and Atmosphere

Prerequisite 1 – Fundamental Commissioning of Building Energy Systems

Note:  Though prerequisites do not contribute to a projects point score, they are mandatory and MUST be met for a project to receive LEED Canada – NC certification.

Credit 3 – Enhanced Commissioning

Note: Building commissioning is a quality assurance method that is implemented to verify and ensure that fundamental building elements and systems are designed, installed and calibrated to operate as intended.  Effective commissioning will ensure that staff are properly trained in the maintenance and operation of the building resulting in building longevity.  A properly commissioned building can also result in significant operational cost saving as energy efficiency often increases.

1.	General

1.1	INTENT

.1	Inspect, start and test each piece of mechanical equipment. Verify that equipment has been properly installed and is operating at a level which meets specified requirements.

1.2	RELATED requirements

.1	Contractor Start-Up Report Forms:	Division 01.

.2	Mechanical General Requirements:	Section 20 00 13.

.3	Operation and Maintenance [Data] [Manuals]:	Section [20 01 05][20 01 06].

.4	General Mechanical Starting and Testing Requirements:	Section 23 08 13.

.5	Balancing and Adjusting of Mechanical Equipment and Systems:	Section 23 08 83.

1.3	FACTORY TRAINED REPRESENTATIVES

.1	Use factory trained representatives and submit manufacturer's check sheets for starting following specialty equipment:

.1	Air handling units.

.2	Boilers.

.3	Chillers.

.4	Cooling towers.

.5	Compressors and vacuum pumps.

.6	Variable speed drive units.

.7	Air flow measuring stations.

.8	Control components.

.9	Chemical cleaning and treatment.

.10	[                           ].

.2	Use manufacturers factory trained personnel where required to maintain manufacturer's warranty.

2.	Products

Not Used

3.	Execution

3.1	FUEL FIRED EQUIPMENT - BOILERS

.1	Pre-Starting:

.1	Verify that installation is as drawn and specified and in accordance with manufacturer's recommendations.

.2	Complete manufacturer's installation and start-up check sheets and include following items on check sheets:

.1	Boiler is level on housekeeping base.

.2	Flue and chimney installed without visible damage.

.3	No visible damage to boiler jacket.

.4	No visible damage to refractory or combustion chamber.

.5	Check PRVs for correct operation and specified relief pressure. Adjust as required.

.6	Clearances have been provided and piping is flanged for easy removal and servicing.

.7	Heating circuit pipes have been connected to correct ports.

.8	Labels are clearly visible.

.9	Boiler, burner and flue completely clean and free of construction debris.

.10	Burner blower rotates in correct direction.

.11	Pressure and temperature gauges installed.

.12	Controls completed.

.3	Ensure pumps are operational.

.4	Check for proper operation of pressure reducing valve on gas train, including venting.

.5	Ensure boiler fluid level, flow switch and high temperature interlocks are in place.

.6	Obtain following from manufacturer and submit as specified in Section 20 00 13:

.1	All equipment performance selection tables.

.2	Manufacturer's equipment start-up sheets.

.2	Starting:

.1	Start pumps.

.2	Perform starting of boilers and adjustment of burners using manufacturer’s factory trained personnel.

.3	Fill out start-up sheets and attach copy with Contractor Start-Up Report.

.4	Check and record performance of all factory provided boiler protection devices, and firing sequences.

.5	Check and record performance of boiler fluid level, flow switch and high temperature interlocks.

.6	Run-in as recommended or required by manufacturer.

.3	Post Starting:

.1	Perform following tests for each firing rate for high/low burners and for 100%, 66%, and 33% load for modulating burners. Adjust boiler combustion efficiency (%) at each firing rate to that specified or advertised by manufacturer, if latter is higher.

.1	Measure gas pressure on manifold.

.2	Measure combustion air temperature at inlet to burner.

.3	Measure flue gas temperature at boiler discharge.

.4	Perform flue gas analysis. Measure and record flue gas CO2 and O2 concentration.

.5	Measure natural flue draft.

.2	Measure water flow rate, pressure drops, and temperature rise through each boiler.

.3	Inspect expansion tank, make-up water meter, tank pressure, PRV, water level and backflow preventer.

.4	Pre-Interim Acceptance: - Not applicable.

3.2	FUEL FIRED EQUIPMENT - SERVICE WATER HEATERS

.1	Pre-Starting:

.1	Verify that installation is as drawn and specified and in accordance with manufacturer's recommendations.

.2	Complete manufacturer's installation and start-up check sheets and include following items on check sheets:

.1	Heater is level on housekeeping base.

.2	Flue and chimney installed without visible damage.

.3	No visible damage to heater jacket.

.4	No visible damage to refractory or combustion chamber.

.5	Check PRVs for correct operation and specified relief pressure. Adjust as required.

.6	Clearances have been provided and piping is flanged for easy removal and servicing.

.7	Labels are clearly visible.

.8	Heater, burner and flue completely clean and free of construction debris.

.9	Burner blower rotates in correct direction.

.10	Controls completed.

.11	Tank has dielectric unions on piping connections.

.3	Verify that chemical sterilization of piping system is completed.

.4	Ensure circulation pump is operational.

.5	Check for proper operation of pressure reducing valve on gas train, including venting.

.2	Starting:

.1	Ensure pilot is operating.

.2	Ensure tank is full of water, vented and flushed.

.3	Ensure thermostat is set at 50°C.

.4	Start as recommended by manufacturer.

.5	Fill out start-up sheets and attach copy with Contractor Start-Up Report.

.6	Check and record performance of all factory provided protection devices, and firing sequences.

.7	Run-in as recommended or required by manufacturer.

.3	Post-Starting:

.1	Measure gas pressure on manifold.

.2	Measure combustion air temperature at inlet to burner.

.3	Measure flue gas temperature at boiler discharge.

.4	Perform flue gas analysis. Measure and record flue gas CO2 and O2 concentration.

.5	Measure natural flue draft.

.6	Adjust heater combustion efficiency (%) to that specified, or advertised by manufacturer if latter is higher.

.7	Fill tank with cold domestic water and determine tank recovery time.

.4	Pre-Interim Acceptance:

.1	Drain tank, refill and vent.

3.3	FUEL FIRED EQUIPMENT - PACKAGED DIRECT FIRED AIR SYSTEMS

.1	Pre-Starting:

.1	Verify that installation is as drawn and specified and in accordance with manufacturer's recommendations.

.2	Complete manufacturer's installation and start-up check sheets and include following items on check sheets:

.1	Unit is level.

.2	No visible damage to unit casing.

.3	Clearances have been provided.

.4	Discharge air thermostats operational and calibrated.

.5	Roof curb sealed to duct penetration, if applicable.

.6	Filter installed.

.7	Labels are clearly visible.

.8	Controls completed.

.3	Check for proper operation of pressure reducing valve on gas train, including venting.

.4	Ensure burner, fan and damper interlocks are in place.

.5	Lubricate bearings on fan as recommended by manufacturer.

.6	Ensure fan wheel rotates in correct direction without vibration or binding.

.7	Adjust belt to proper alignment and tension.

.2	Starting:

.1	Check correct operation of safety interlocks, including exhaust fans, outside air damper, fan and burner interlocks, CO detector.

.2	Start as recommended by manufacturer.

.3	Fill out start-up sheets and attach copy with Contractor Start-Up Report.

.4	Check and record performance of all factory provided burner protection devices, and firing sequences.

.5	Check summer operation burner firing lockout.

.6	Run-in as required by manufacturer.

.3	Post-Starting:

.1	Perform a discharge air combustion products analysis and adjust burner for peak efficiency over entire turn down range of burner.

.2	Measure gas pressure on manifold.

.3	Measure air flow on high and low fire to ensure sufficient velocities across burner profile plate.

.4	Adjust belt tension and change pulley sheaves to desired air flow.

.5	Check to see that following occurs:

.1	Exhaust fans are interlocked with unit.

.2	High temperature  limit for  correct operation and calibration.

.3	Air flow lockout for proper operation.

.4	High and low gas pressure switches for proper operation.

.5	Burner turn down and flame stability.

.6	Vibration isolators are free.

.7	Calibrate discharge air control and set to specified level.

.4	Pre-Interim Acceptance:

.1	Replace filters.

.2	Lubricate bearings.

.3	Adjust belt tension.

3.4	FUEL FIRED EQUIPMENT - FORCED AIR FURNACES

.1	Pre-Starting:

.1	Verify that installation is as drawn and specified and in accordance with manufacturer's recommendations.

.2	Complete manufacturer's installation and start-up check sheets and include following items on check sheets:

.1	Furnace is level on housekeeping base.

.2	Flue and chimney installed without visible damage.

.3	No visible damage to furnace jacket.

.4	No visible damage to combustion chamber.

.5	Clearances to combustibles have been maintained.

.6	Clearances have been provided for servicing.

.7	Labels are clearly visible.

.8	Furnace and flue are completely clean and free of construction debris.

.9	Filter installed.

.10	Controls completed.

.11	Combustion and make-up air have been provided.

.12	Gas line is complete and purged.

.3	Lubricate bearings on fan as recommended by manufacturer.

.4	Ensure fan wheel rotates in correct direction without vibration or binding.

.5	Adjust belt to proper alignment and tension.

.2	Starting:

.1	Start furnaces as recommended by manufacturer.

.2	Fill out start-up sheets and attach copy with Contractor Start-Up Report.

.3	Check and record performance of all factory provided furnace protection devices, and firing sequences.

.4	Run-in as required by manufacturer.

.3	Post-Starting:

.1	Measure gas pressure on manifold.

.2	Measure combustion air temperature at inlet to combustion chamber.

.3	Measure flue gas temperature at furnace discharge.

.4	Perform flue gas analysis.  Measure and record flue gas CO2 and O2 concentration.

.5	Measure natural flue draft.

.6	Adjust burner for peak efficiency. Adjust pilot to stable flame.

.7	Check for backdraft under full operation.

.8	Determine furnace room negative pressure.

.9	Confirm humidifier interlock.

.10	Calibrate thermostats.

.11	Adjust heat exchanger preheat and postcool fan timing controls.

.12	Adjust and check high temperature limits.

.13	Check fan on-off-auto switch for proper operation.

.14	Check heat-cool switch for proper operation, if applicable.

.4	Pre-Interim Acceptance:

.1	Replace filters.

.2	Lubricate bearings.

.3	Adjust belt tension.

3.5	FUEL FIRED EQUIPMENT - GAS FIRED UNIT HEATERS

.1	Pre-Starting:

.1	Verify that installation is as drawn and specified and in accordance with manufacturer's recommendations.

.2	Complete manufacturer's installation and start-up check sheets and include following items on check sheets:

.1	Unit is level.

.2	Flue and chimney installed without visible damage.

.3	No visible damage to unit casing.

.4	No visible damage to combustion chamber.

.5	Clearances to combustibles have been maintained.

.6	Clearances have been provided for servicing.

.7	Labels are clearly visible.

.8	Combustion chamber and flue completely clean and free of construction debris.

.9	Controls completed.

.10	Combustion air has been provided.

.11	Gas line is complete and purged.

.3	Lubricate bearings on fan as recommended by manufacturer.

.4	Ensure fan wheel rotates in correct direction without vibration or binding.

.2	Starting:

.1	Start gas fired unit heaters as recommended by manufacturer.

.2	Fill out start-up sheets and attach copy with Contractor Start-Up Report.

.3	Check and record performance of all factory provided unit heater protection devices, and firing sequences.

.4	Run-in as recommended or required by manufacturer.

.3	Post-Starting:

.1	Measure gas pressure on manifold.

.2	Measure combustion air temperature at inlet to combustion chamber.

.3	Measure flue gas temperature at furnace discharge.

.4	Perform flue gas analysis. Measure and record flue gas CO2 and O2 concentration.

.5	Measure natural flue draft.

.6	Adjust burner for peak efficiency. Adjust pilot to stable flame.

.7	Check for backdraft under full operation.

.8	Calibrate thermostats.

.9	Adjust heat exchanger preheat and postcool fan timing controls.

.10	Adjust and check high temperature limits.

.4	Pre-Interim Acceptance:

.1	Lubricate bearings.

.2	Adjust belt tension.

3.6	FUEL FIRED EQUIPMENT - PACKAGED ROOFTOP FURNACE WITH COOLING

.1	Pre-Starting:

.1	Verify that installation is as drawn and specified and in accordance with manufacturer's recommendations.

.2	Complete manufacturer's installation and start-up check sheets and include following items on check sheets:

.1	Packaged unit is level on housekeeping base, and curbs are properly flashed to unit and to roof.

.2	No visible damage to unit casing.

.3	No visible damage to furnace combustion chamber.

.4	No visible damage to DX compressor, air cooled condenser coil or fans.

.5	Clearances have been provided for servicing.

.6	Labels are clearly visible.

.7	Furnace, flue and DX condenser completely clean and free of construction debris.

.8	Controls completed.

.9	Remove shipping bolts, blocks and tie-down straps.

.10	Filter installed.

.11	Adjust vibration isolators.

.12	Gas line is complete and purged.

.13	Check burner and controls are suitable for operation down to -40°C.

.14	Check acoustic insulation.

.15	Check operation of barometric dampers.

.3	Lubricate bearings on fan as recommended by manufacturer.

.4	Ensure fan wheel rotates in correct direction without vibration or binding.

.5	Adjust belt to proper alignment and tension.

.2	Starting:

.1	Start furnace and DX chiller in accordance with manufacturer’s recommendations.

.2	Perform starting of DX chiller in summer only.

.3	Fill out start-up sheets and attach copy with Contractor Start-Up Report.

.4	Check and record performance of all factory provided furnace and DX chiller interlocks and protection devices, and furnace firing sequences.

.5	Run-in as recommended or required by manufacturer.

.3	Post-Starting:

.1	Perform following operations for both minimum and maximum firing, and adjust burner for peak efficiency. Adjust pilot to stable flame.

.1	Measure gas pressure on manifold.

.2	Measure combustion air temperature at inlet to combustion chamber.

.3	Measure flue gas temperature at furnace discharge.

.4	Perform flue gas analysis.  Measure and record flue gas CO2 and O2 concentration.

.2	Measure furnace air on and off dry bulb temperatures and air volume at maximum firing rate. Calculate useful heat to supply air.

.3	Check for backdraft under full operation.

.4	Calibrate thermostats.

.5	Adjust and check high temperature limits.

.6	Check internal isolators.

.7	Check outside air damper for proper stroke and interlock with return air dampers.

.8	Check controls for correct sequencing of furnace, mixing section dampers, DX chiller and normal and emergency shutdown.

.9	Start chiller, measure and record following:

.1	Leaving coil air dry and wet bulb temperatures.

.2	Entering coil air dry and wet bulb temperatures.

.3	Outside air dry bulb temperature.

.4	Air cooled condenser discharge dry bulb temperature.

.10	Measure and record following minimum and maximum air flows. Plot fan volumes on fan curve:

.1	Supply volume.

.2	Return volume.

.3	Relief air volume.

.4	Outside intake air volume.

.11	Simulate maximum cooling demand and check:

.1	Compressor refrigerant suction and hot gas pressures.

.2	Use smoke to check if there is any short circuiting of air through condenser or from condenser to fresh air intake.

.12	Verify operation of remote panel, including pilot light operation, failure modes, and check:

.1	High-limit-heat exchanger.

.2	Warm-up for morning cycle.

.3	Freezestat operation.

.4	Free-cooling mode outdoor air changeover.

.5	Alarms.

.4	Pre-Interim Acceptance:

.1	Replace air filters

.2	Vacuum clean heat exchanger, cooling and condenser coils.

.3	Lubricate bearings.

.4	Adjust belt tension.

.5	Check operation of power vents.

3.7	FLUID HANDLING EQUIPMENT - PUMPS

.1	Pre-Starting:

.1	Verify that installation is as drawn and specified and in accordance with manufacturer's recommendations.

.2	Complete manufacturer's installation and start-up check sheets and include following items on check sheets:

.1	Pump is level.

.2	Isolation valves, strainers, check valve, pressure gauges, by-pass filter and flow meter are installed properly.

.3	Pump suction has sufficient length of straight run piping.

.4	Air has been completely bled off piping system.

.5	Expansion tank is charged and on-line.

.6	Strainers have clean screens in place.

.7	Where specified for large pumps, check pump base vibration isolation and flexible connections on water pipes are properly installed.

.8	Nameplate is readily visible.

.9	Check clearance space is adequate for pump servicing and removal.

.2	Starting:

.1	Start as recommended by manufacturer.

.2	Fill out start-up sheets and attach copy with Contractor Start-Up Report.

.3	Check impeller is rotating in correct direction.

.3	Post Starting:

.1	Run-in pumps for minimum 12 continuous hours.

.2	Ensure flows through parallel pumps are equally balanced.

.3	Ensure mechanical seals do not leak, or packing gland type seals are wetted.

.4	Check pump NPSH - net positive suction head.

.5	Where vibration isolation is specified, check for correct static deflection of unit vibration isolators, and that start up and shut down deflection is within resilience limits of isolators and flexible connections.

.6	Verify that motor has sufficient air flow through casing to provide cooling.

.4	Pre-Interim Acceptance:

.1	Clean strainers.

.2	Replace shaft seals if pump has been used to degrease system.

3.8	FLUID HANDLING EQUIPMENT - HEAT EXCHANGERS

.1	Pre-Starting:

.1	Verify that installation is as drawn and specified and in accordance with manufacturer's recommendations.

.2	Complete manufacturer's installation and start-up check sheets and include following items on check sheets:

.1	Vessel is level on housekeeping base.

.2	PRVs are properly installed and operational.

.3	Clearances have been provided and piping is flanged for easy removal and servicing.

.4	Primary and Secondary circuit pipes have been connected to correct ports.

.5	Nameplate and labels are clearly visible.

.6	Unit is clean of foreign matter.  Remove heads to inspect for cleanliness as required.

.7	Control valve piping is connected for correct flow through valve body and for required fail safe action of valve.

.8	Insulation is complete.

.3	Ensure Primary and Secondary side pumps are complete and operational.

.2	Starting:  not applicable.

.3	Starting:  Refer to Section 23 08 83 - Balancing and Adjusting of Mechanical Equipment and Systems.

.4	Pre-Interim Acceptance: not applicable.

3.9	FLUID HANDLING EQUIPMENT - COILS

.1	Pre-Starting:

.1	Verify that installation is as drawn and specified and in accordance with manufacturer's recommendations.

.2	Complete manufacturer's installation and start-up check sheets and include following items on check sheets:

.1	Pipe connections have been correctly made for counter current heat exchange between air and fluid.

.2	Clearances have been provided and piping is flanged for easy removal and servicing.

.3	Coil air vent and drain valve and deadleg drain valves have been provided.

.4	Coil is sloped to ensure complete drain down.

.5	Pressure and temperature tappings, Pete's plugs, have been provided.

.6	Fins inspected and combed straight as required.

.7	Cooling coil drain pan and trapped drain line installed correctly.

.8	Labels are clearly visible

.9	Control valve piping is connected for correct flow through valve body and for required fail safe action of valve.

.2	Starting:

.1	Check operation of cooling coil condensate drain with supply fan at maximum air flow.  Ensure that condensate will drain away against maximum suction pressure of supply fan. Check for and eliminate condensate carry over at maximum air velocity.

.3	Post-Starting:  refer to Section 23 08 83 - Balancing and Adjusting of Mechanical Equipment and Systems.

.4	Pre-Interim Acceptance:  not applicable.

3.10	FLUID HANDLING EQUIPMENT - ELECTRIC STEAM GRID HUMIDIFIERS

.1	Pre-Starting:

.1	Verify that installation is as drawn and specified and in accordance with manufacturer's recommendations.

.2	Complete manufacturer's installation and start-up check sheets and include following items on check sheets:

.1	Manifold slopes back to unit to drain condensate away from duct.

.2	Clearances allowed for servicing.

.3	Interlocks and safeties operational.

.4	Make-up water and drain connections complete.

.2	Starting:

.1	Start as recommended by manufacturer.

.2	Fill out manufacturer's check sheets.

.3	Post-Starting:

.1	Check humidistat control of unit.

.2	Check automatic blowdown cycle.

.3	Measure humidifier steaming rate.

.4	Pre-Interim Acceptance: not applicable

3.11	FLUID HANDLING EQUIPMENT - WETTED MEDIA HUMIDIFIERS

.1	Pre-Starting:

.1	Check that installation is as drawn and specified and in accordance with manufacturer's recommendations.  Check following:

.1	Header troff is level and evenly distributes water across the media.

.2	Clearance allowed for servicing and media replacement.

.3	Basin blowdown and chemical dosing complete.

.4	Make-up water and drain connections complete.

.2	Starting:

.1	Check operation of fully wetted media with supply fan at maximum air volume.

.2	Check for and eliminate water carry over at maximum air velocity.

.3	Ensure that any water in supply fan plenum will drain away against maximum suction pressure of supply fan.

.3	Post-Starting:

.1	Check uniform wetting of media.

.2	Check automatic blowdown cycle.

.3	Check automatic algicide and fungicide dosing of humidifier basin.

.4	Measure humidifier performance.

.4	Pre-Interim Acceptance: not applicable.

3.12	FLUID HANDLING EQUIPMENT - COOLING TOWERS

.1	Pre-Starting:

.1	Verify that installation is as drawn and specified and in accordance with manufacturer's recommendations.

.2	Complete manufacturer's installation and start-up check sheets and include following items on check sheets:

.1	Clean entire unit and wash down basins.

.2	Ensure all accessories are properly installed.

.3	Check water make-up float.

.4	Check clearances for air flow and for tower servicing.

.5	Check for vibration isolation and structural support.

.3	Obtain wet bulb, tower size and packing selection tables from manufacturer.

.4	Lubricate bearings on fans and shaft as recommended by manufacturer.

.5	Ensure fan wheels rotate in correct direction without vibration or binding.

.6	Adjust belts to proper alignment and tension.

.2	Starting:

.1	Start as recommended by manufacturer.

.2	Fill out manufacturer's check sheets.

.3	Post-Starting:

.1	Check water level in tower basin.

.2	Check operation of tower basin automatic blowdown, and controlling device.

.3	Check operation of tower basin, make-up line and condenser pipe automatic freeze protect dump, and controlling device.

.4	Check operation of basin immersion heater and control thermostat.

.5	Ensure system chemical treatment is properly working, and measure chemical treatment levels.

.6	Check that tower discharge plume is not recirculating into air intakes.

.4	Pre-Interim Acceptance:

.1	Check tower for proper sump level.

.2	Check and document chemical treatment level.

.3	Lubricate bearings.

.4	Check belts for tension and wear.

3.13	FLUID HANDLING EQUIPMENT - CHILLERS

.1	Pre-Starting:

.1	Verify that installation is as drawn and specified and in accordance with manufacturer's recommendations.

.2	Complete manufacturer's installation and start-up check sheets and include following items on check sheets:

.1	No physical damage to unit has occurred during construction.

.2	Unit is level on housekeeping base.

.3	Check that chiller base vibration isolation and flexible connections on water pipes are properly installed.

.4	Clearances have been provided and piping is flanged for easy removal, servicing and tube cleaning.

.5	Chilled and condenser water circuit pipes have been connected to correct ports.

.6	Labels are clearly visible.

.7	Oil levels are as recommended by manufacturer.

.8	Refrigerant charge is sufficient and leak tested.

.9	Shipping skids/blocks/straps are removed.

.10	Unit has adequate ventilation, as specified in CSA B52-95.

.11	Unit condenser refrigerant pressure relief is vented to ambient.

.12	Thermometers, pressure gauges installed.

.13	Control systems and safety interlocks are complete.

.14	Pumps completed and started.

.15	Crankcase heater is on a minimum of 24 hours prior to chiller start-up.

.3	Obtain following from manufacturer and submit as specified in section 20 00 13:

.1	All equipment performance selection tables.

.2	Manufacturer's equipment start-up sheets.

.2	Starting:

.1	Start chillers using manufacturer’s factory trained personnel.

.2	Fill out start-up sheets and attach copy with Contractor Start-Up Report.

.3	Check and record performance of all factory provided chiller protection devices.

.4	Check and record performance of all chiller flow, pump and low temperature interlocks installed or provided by other trades.

.3	Post-Starting:

.1	Run in chiller as recommended by manufacturer.

.2	Check for correct static deflection of the unit vibration isolators, and that start-up and shut down deflection is within resilience limits.

.4	Pre-Interim Acceptance:

.1	Check refrigerant level and charge as necessary.

.2	Check oil level and fill as necessary.

.3	Check refrigerant dryer and change as necessary.

3.14	FLUID HANDLING EQUIPMENT - MISCELLANEOUS

.1	Gauges and Thermometers:

.1	Confirm all gauges and thermometers can be read from the floor level and are installed as recommended by manufacturer.

.2	Calibrate.

.2	Verify following equipment is installed as recommended by manufacturer. Fill out manufacturer's start-up sheets:

.1	PRVs.

.2	Air eliminators.

.3	Strainers.

.4	Check valves.

.5	Balancing valves.

.6	Plumbing fixtures.

.7	Backflow preventers.

.8	Vacuum breakers.

3.15	AIR HANDLING EQUIPMENT - AIR HANDLING UNITS

.1	Pre-Starting:

.1	Check that installation is as drawn and specified and in accordance with manufacturer's recommendations.

.2	Complete manufacturer's installation and start-up check sheets including following:

.1	Air blender, mixing baffles.

.2	Fresh, Exhaust and Recirculation air motorized dampers, operation and size.

.3	Filters.

.4	Check that fan base vibration isolation and flexible connections to ductwork are properly installed.

.5	Special features, access doors, liners, inlet vanes, labels.

.6	For variable volume systems, ensure variable volume/speed controller is operational.

.7	Ensure silencers are installed.

.2	Lubricate bearings on fans as recommended by manufacturer.  Ensure fan wheels rotate in correct direction without binding.  Adjust belts to proper alignment and tension.

.3	Vacuum clean air systems.

.4	Ensure temporary filters are installed.  Never operate system without filters installed.

.5	Ensure all balancing and fire dampers are open and ductwork is complete.  For VAV systems ensure at least 60% of boxes are open.

.6	Ensure all coils are in operation.  If outside air temperature is less than 2°C ensure coils are dry or filled with glycol.

.7	On parallel fan systems ensure backdraft dampers are installed.

.8	Ensure electrical connections are complete and system disconnects are within sight of unit.

.9	Ensure controls are operational.

.10	Ensure inlet and discharge duct geometry is correct.

.2	Starting:

.1	Follow manufacturer's recommendations.

.3	Post-Starting:

.1	Start fan, for variable speed fans run up to maximum speed, and check for vibration free operation.

.2	Check for correct static deflection of unit vibration isolators, and that start-up and shut down deflection is within resilience limits.

.3	Run for one day and check filters, coils, and humidifier for bypass.  Seal as required.

.4	Check that bearings are not overheating.

.4	Pre-Interim Acceptance:

.1	Replace temporary filters with permanent filters.

.2	Vacuum clean heating and cooling coils.

.3	Lubricate bearings.

.4	Check belts for tension and wear.

3.16	AIR HANDLING EQUIPMENT - FANS

.1	Pre-Starting:

.1	Check that installation is as drawn and specified and in accordance with manufacturer's recommendations.

.2	Complete manufacturer's installation and start-up check sheets including following:

.1	Backdraft dampers.

.2	Accessories.

.3	Special features.

.4	Check that fan base vibration isolation and flexible connections to ductwork are properly installed.

.3	Lubricate bearings on fans as recommended by manufacturer.

.4	Ensure fan wheels rotate in correct direction without binding.

.5	Adjust belts to proper alignment and tension.

.6	Ensure ductwork and fan casing is free of dirt or foreign material.

.7	Ensure electrical connections are complete and disconnect is within sight of fan.

.8	Ensure inlet and discharge duct geometry is correct.

.2	Starting:

.1	Follow manufacturer's recommendations.

.3	Post-Starting:

.1	Start fan, for variable speed fans run up to maximum speed, and check for vibration free operation.

.2	Check for correct static deflection of unit vibration isolators, and that start-up and shut down deflection is within resilience limits.

.3	Check that bearings are not over heating.

.4	Pre-Interim Acceptance:

.1	Lubricate bearings.

.2	Check belts for tension and wear.

3.17	AIR HANDLING EQUIPMENT - AIR FLOW MEASURING STATIONS

.1	Pre-Starting:

.1	Check that installation is as drawn and specified and in accordance with manufacturer's recommendations.  Check following:

.1	Manufacturer's recommended length of duct ahead and behind flow station.

.2	Straightening vane installed before flow station.

.3	Flow station located away from fan discharges, silencer outlets, duct branches, etc.

.4	No take off branches have been placed ahead of measuring station location.

.5	Straight section of duct adjacent to flow station to take air flow measurement duct traverses.

.6	Air flow measuring station sized for adequate velocity pressure range, and transducer range is compatible with design velocity range of flow station.

.2	Starting:  not applicable.

.3	Post-Starting:  refer to Section 23 08 83.

.4	Pre-Interim Acceptance:  not applicable.

3.18	AIR HANDLING EQUIPMENT - VAV BOXES

.1	Pre-Starting:

.1	Check that each installation is as drawn and specified and in accordance with manufacturer's recommendations.  Check following:

.1	Inlet duct connection:

.1	shall have four duct diameters to box inlet.

.2	shall not have more than 150 mm flexible connection between duct and box.

.3	shall not have flow straightening vanes.

.2	Access to controls.

.3	Completeness of control connections.

.4	Silencer/acoustic duct.

.5	No damage to exterior casing or controls.

.6	Box support adequate.

.7	Nameplate and identification tag is visible.

.2	Starting:  not applicable.

.3	Post-Starting:  refer to Section 23 08 83.

.4	Pre-Interim Acceptance:  not applicable.

3.19	AIR HANDLING EQUIPMENT - UNIT AND CABINET HEATERS

.1	Pre-Starting:

.1	Check each installation is as drawn and specified and in accordance with manufacturer's recommendations.  Check following:

.1	Piping connections.

.2	Unit vibration isolation.

.3	Ducting connections.

.4	Controls.

.5	Disconnect switches.

.6	Unit clean.

.2	Starting:  as recommended by manufacturer.

.3	Post-Starting:  refer to Section 23 08 83.

.4	Pre-Interim Acceptance:  not applicable.

3.20	AIR HANDLING EQUIPMENT - MISCELLANEOUS

.1	Refer to Section 23 08 83.

3.21	MISCELLANEOUS EQUIPMENT - VARIABLE SPEED DRIVE UNITS

.1	Pre-Starting:

.1	Obtain following from manufacturer and submit as specified in Section 20 00 13.

.1	All equipment performance selection tables.

.2	Manufacturer's equipment start-up sheets.

.2	Verify that installation is as specified and in accordance with manufacturer's recommendations.

.2	Starting:

.1	Start variable speed controllers and motor powered from each drive using manufacturer’s factory trained personnel.

.2	Fill out start-up sheets and attach copy with Contractor Start-Up Report.

.3	Check and record operation of all factory provided protection devices.

.4	Run-in as required and recommended by manufacturer.

.3	Post Starting:

.1	Run motor up to maximum speed, check ampere draw.  Check and set overloads.

.2	Check manual override control and manual speed control of motor

.3	Put speed controller in automatic, command motor to full speed and check that motor speed ramp operates correctly accelerating motor to maximum speed without tripping.  Command motor to minimum speed and observe controlled deceleration of motor.

.4	Pre-Interim Acceptance:  not applicable.

3.22	MISCELLANEOUS EQUIPMENT - TANKS

.1	Pre-Starting:

.1	Verify that installation is as drawn and specified and in accordance with manufacturer's recommendations.  Check following:

.1	Tank is level on housekeeping base.

.2	No visible damage to vessel.

.3	Check PRVs for correct operation and specified relief pressure. Adjust as required.

.4	Clearances have been provided and piping is flanged for easy removal and servicing.

.5	Labels are clearly visible.

.6	Controls, gauges, alarm devices, etc. are operational.

.7	Access ports/manholes provided.

.8	Piping sizes - inlet/outlet are correct.

.9	Lining is intact and not damaged.

.10	Tank has dielectric unions on piping connections.

.2	Starting:  not applicable.

.3	Post-Starting:

.1	Verify operation of:

.1	Drain line.

.2	Make-up line if applicable.

.3	Gauge glass.

.4	Diaphragm if applicable.

.4	Pre-Interim Acceptable: not applicable.

3.23	MISCELLANEOUS EQUIPMENT - AIR COOLED CONDENSERS

.1	Pre-Starting:

.1	Check that installation is as drawn and specified and in accordance with manufacturer's recommendations.

.2	Complete manufacturer's installation and start-up check sheets including following:

.1	No physical damage to unit has occurred.

.2	All access doors move freely and are weathertight.

.3	Unit is free of foreign debris.

.4	All bolts, screws are tight.

.5	Condenser base vibration isolation and flexible connections on refrigerant pipes are properly installed.

.6	Controls complete.

.7	Check acoustic insulation.

.8	Fan guards are installed.

.3	Lubricate bearings on fans as recommended by manufacturer.

.4	Ensure fan wheels rotate in correct direction without binding.

.5	Adjust belt to proper alignment and tension.

.2	Starting:

.1	Start in accordance with manufacturer's instructions.

.2	Complete manufacturers starting check sheet.

.3	Post-Starting:

.1	Ensure all fan guards are tight.

.2	Check air flows over coils.

.3	Check operation of condenser capacity control device.

.4	Ensure vibration isolation and flexible connections to unit properly damp vibration transmission to structure.

.4	Pre-Interim Acceptance:

.1	Lubricate bearings.

.2	Adjust belt tension.

3.24	MISCELLANEOUS EQUIPMENT - COMPRESSORS AND VACUUM PUMPS

.1	Pre-Starting:

.1	Check following after installation:

.1	No physical damage occurred during construction.

.2	Unit base vibration isolation and flexible connections on service pipes are properly installed.

.3	Adjust belts to proper alignment and tension.

.4	Belt guards are in place.

.5	Unit is level.

.6	Fused disconnect located at unit.

.7	Air dryer properly installed.

.8	Automatic condensate drain installed.

.9	Lubricate bearings.

.2	Starting:

.1	Start unit in accordance with manufacturer's instructions.

.2	Fill out manufacturer's start-up sheets.

.3	Post-Starting:

.1	Check for correct static deflection of unit vibration isolators, and that start-up and shut down deflection is within resilience limits.

.2	Ensure sufficient outdoor air is available to unit.

.3	Check to ensure no oil carryover in air stream.

.4	Air dryer is operating and chilling air to correct temperature.  Condensate is being removed from air line.

.5	Pressure regulators and PRV are correctly set.

.6	Automatic condensate drain valve is operating correctly.

.4	Pre-Interim Acceptance:

.1	Change air filter in unit.

.2	Check for oil carryover into air supply.

.3	Check oil levels, and refill as necessary.

.4	Change air line filter cartridges.

.5	Adjust belt tension.

3.25	MISCELLANEOUS EQUIPMENT - PACKAGED AIR CONDITIONING UNITS

.1	Pre-Starting:

.1	After installation check following:

.1	No damage to unit.

.2	Unit is level.

.3	Drain pan and drain line installed correctly.

.4	Compressor base vibration isolation and flexible connections on refrigerant pipes are properly installed.

.5	Make-up water complete.

.6	Humidifier flush water piping complete.

.7	Ductwork complete.

.8	Bearings lubricated.

.9	Filters installed and clean.

.2	Starting:

.1	Start unit in accordance with manufacturer’s instructions.

.2	Fill out manufacturer's check sheets.

.3	Post-Starting: refer to Section 23 08 83 - Balancing and Adjusting of Mechanical Equipment and Systems.

.4	Pre-Interim Acceptance:

.1	Change filters.

.2	Flush humidifier.

3.26	MISCELLANEOUS EQUIPMENT - FIRE EXTINGUISHERS

.1	Check the number, make, model and capacity of each portable fire extinguisher.

.2	Check the pressure drop on each extinguisher over 20 day period. Replace units loosing charge.

.3	Check that all cabinets are clean and door latch functions correctly.

3.27	MISCELLANEOUS EQUIPMENT - FIRE HOSE CABINETS

.1	Check the number, make and model of each cabinet.

.2	Ensure doors open fully and do not block exit or exit corridors.

.3	Check that all cabinets are clean and door latch functions correctly.

.4	Adjust PRV's and record pressures.

.5	Check 32 mm hose connection, 65 mm fire department connection, fire hose and nozzle and fire extinguisher as applicable.

END OF SECTION