Section Cover Page

Section 23 08 33 Mechanical Systems 2010-12-31 Starting and Testing

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if project: .1 is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

Use this Section to specify all Mechanical Systems Starting and Testing Requirements for Division 23.  Do not specify these requirements in individual Mechanical Work related technical sections; include cross-references to this Section 23 08 33 only.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Data Sheet - Reference Standards

.3	Specification Section Text:

1.	General

1.1	Intent

1.2	Related Requirements

1.3	Reference Documents

1.4	Factory Trained Representatives

2.	Products

Not Used

3.	Execution

3.1	Operational Tests

3.2	Air Systems

3.3	Hydronic Systems

3.4	Steam Systems

3.5	Control Systems

3.6	Domestic Water Systems

3.7	Plumbing Drainage Systems

3.8	Standpipe and Sprinkler Systems

LEED Notes:

Refer to Section 01 35 18 – LEED Requirements for:

1.	Requirements necessary for this project to obtain points required for certification.

2.	Confirmation of LEED prerequisites and credits affecting this Section; not all are mandatory for certification

Maintain built-in sustainability regardless of LEED requirements for:

.1	Recycling, reuse of materials, components and assemblies.

.2	Diversion of construction waste from landfills.

.3	Use of recycled materials, local materials, rapidly renewable and durable materials.

.4	Maintain healthy indoor environment during constructing.

.5	Provide for thermal comfort, access to views and daylight for indoor spaces.

.6	Foster innovation into facility design and planning.

LEED Credits:

Energy and Atmosphere

Prerequisite 1 – Fundamental Commissioning of Building Energy Systems

Note:  Though prerequisites do not contribute to a projects point score, they are mandatory and MUST be met for a project to receive LEED Canada – NC certification.

Credit 3 – Enhanced Commissioning

Note: Building commissioning is a quality assurance method that is implemented to verify and ensure that fundamental building elements and systems are designed, installed and calibrated to operate as intended.  Effective commissioning will ensure that staff are properly trained in the maintenance and operation of the building resulting in building longevity.  A properly commissioned building can also result in significant operational cost saving as energy efficiency often increases.

1.	General

1.1	INTENT

.1	Inspect, start-up and commission each system to prove that each system meets its specified operating criteria.

1.2	RELATED requirements

.1	Construction Schedules:	Division 01.

.2	Contractor Start-up Report Forms:	Division 01.

.3	Cleaning Domestic Water Systems:	Section 22 11 20.

.4	General Mechanical Starting and Testing Requirements:	Section 23 08 13.

.5	Mechanical Equipment Starting and Testing:	Section 23 08 23.

.6	Pressure Testing:	Section 23 08 43.

.7	Balancing and Adjusting of Mechanical Equipment and Systems:	Section 23 08 83.

.8	Mechanical Equipment and Systems Demonstration and Instruction:	Section 23 08 93.

.9	EMCS Start-up and Testing:	Section 23 08 95.

.10	Energy Management and Control System (EMCS)
General Requirements:	Section 23 09 23.

.11	EMCS Control Sequences:	Section 23 09 93.

.12	Cleaning and Chemical Treatment - General Requirements	Section 23 25 02.

.13	Cleaning and Chemical Treatment of Hydronic System:	Section 23 25 13.

.14	Cleaning and Chemical Treatment of Steam Boiler Systems:	Section 23 25 19.

.15	Cleaning and Chemical Treatment of Condenser Systems:	Section 23 25 20.

.16	Cleaning and Chemical Treatment of Glycol Systems:	Section 23 25 26.

.17	Cleaning and Chemical treatment of Air Washer Humidifier Systems:	Section 23 84 93.

.18	Fire Alarm System Verification:	Division 26.

.19	Sewer System	Section 33 30 10.

.20	Sanitary Sewage Force Main System	Section 33 34 05.

1.3	REFERENCE DOCUMENTS

.1	Canadian Standards Association (CSA):

| .1 | NFPA 13-2010 | Standard for the Installation of Sprinkler Systems |
| --- | --- | --- |
| .2 | NFPA 14-2010 | Standards for the Installation of Standpipe and Hose Systems |
| .3 | NFPA 20-2010 | Standards for the of Stationary Pumps for Fire Protection |

1.4	FACTORY TRAINED REPRESENTATIVES

.1	Use factory trained representatives for starting of the following specialty systems:

.1	Controls

.2	Sprinkler

.3	[                                         ]

.2	Use manufacturers' representatives where required to maintain manufacturers' warranties.

2.	Products

Not Used.

3.	Execution

3.1	OPERATIONAL TESTS

.1	Conduct operational tests after mechanical installations have been completed and pressure tested to demonstrate that equipment and systems meet specified performance requirements. Conduct these tests as soon as conditions permit. Make changes, repairs, adjustments, and replacements required as tests may indicate.

.2	Conduct pre-operational tests, processes and inspections in presence of the Minister, if so requested by the Minister.

.3	Conduct final operational tests in presence of the Minister. Vary loads to illustrate start-up and shut down sequences. Simulate emergency conditions for safety shut downs, with automatic and manual reset. Repair and retest defects until satisfactory results are achieved. Make final adjustments to suit exact building conditions.

3.2	AIR SYSTEMS

.1	Inspect air systems including ductwork layout, support, and vibration isolation before pressure testing any section of ductwork. Notify Minister when work is ready for inspection.

.2	Power vacuum all ducts 900 mm [   ] and larger.

.3	Pressure test sections of ductwork, in accordance with Section 23 08 43, prior to application of insulation or concealment. Notify Minister [two] [   ] working days prior to any system pressure test.

.4	Test drop fire dampers in accordance with Section 23 08 83. Notify Minister [two] [   ] working days prior to fire damper testing.

.5	Air Handling Unit: start-up and performance verification [using manufacturer’s representative]. Provide [two] [   ] working days notice to the Minister.

.6	Start up coil circulators, humidifier spray pumps, exhaust air systems, etc.

SPEC NOTE:  Include clause 3.2.7 for Variable volume systems only.

.7	Variable Volume Air Systems:

.1	Performance test and calibrate Air Flow Measuring Stations in accordance with Sections 23 08 83 and 23 08 95.

.2	Prove that fan variable volume controls are operational including EMCS control software.

.8	Demonstrate operation of mixing section, blender, filters, freeze protect, fire alarm interlocks, etc.

.9	Performance test fans, coils, humidifier, etc. in accordance with Section 23 08 83.

.10	Balance air systems in accordance with Section 23 08 83. Complete and submit Air Systems balance report to Minister.

.11	If necessary change pulley drives to correct volume up or down on constant volume systems, and to correct volume up on variable volume systems.

.12	Perform acoustic survey in accordance with Section 23 08 83. Rectify any noise problems encountered.

.13	Complete and submit Air Systems Start-up report as specified in Section 23 08 13.

.14	Conduct Mechanical Systems Demonstration and Instruction in accordance with Section 23 08 93.

3.3	HYDRONIC SYSTEMS

.1	Inspect piping layout, pipe support, expansion provisions, slope for draining and venting, vibration isolation, etc. before pressure testing any section of pipework. Notify Minister when work is ready for inspection.

.2	Pressure test sections of pipework, in accordance with Section 23 08 43, prior to application of insulation or to concealment.

.3	Pressure test each completed system, in accordance with Section 23 08 43, before any equipment is started. Notify Minister [two] [   ] working days prior to any system pressure test.

.4	Start-up pumps.

.5	Heating appliance: perform start-up and performance verification [using manufacturer’s representative]. Provide [two] [   ] working days notice to the Minister.

.6	Rough balance system to ensure fluid circulation in every circuit. Rough balance cooling systems by velocity or pressure drop measurements at each circuit  or component. Rough balance heating systems by temperature drop measurement.

.7	Chemically clean water filled system in accordance with Section 23 25 13 and glycol filled systems in accordance with 23 25 26. Notify Minister [two] [   ] working days prior to any system cleaning.

.8 	Chemically treat water filled systems in accordance with Section 23 25 13 and glycol systems in accordance with Section 23 25 26.

.9	Fine balance systems in accordance with Section 23 08 83. Complete and submit Hydronic Systems balance report to Minister.

.10	Charge chiller with refrigerant.

.11	Chiller [and cooling tower]: perform start-up and performance testing using manufacturer’s representative. Provide [two] [   ] working days notice to the Minister.

.12	Check system for fluid or pump noise in pipes. Rectify as necessary.

.13	Provided the flow rate exceeds that specified, shave impeller on pumps larger than 1.5 kW if current draw exceeds motor full load amps or if there is excess flow which results in excessive pipe noise in adjacent occupied areas.

.14	Complete and submit Hydronic systems Start-up report as specified in Section 23 08 13.

.15	Conduct Mechanical Equipment and Systems Demonstration and Instruction in accordance with Section 23 08 93.

3.4	STEAM SYSTEMS

.1	Inspect steam systems including piping layout, pipe support, expansion  provisions, slope for draining and venting, and vibration  isolation, before pressure testing any section of  pipework. Notify Minister when work is ready for  inspection.

.2	Pressure test sections of pipework, in accordance with Section 23 08 43, prior to application of insulation or to concealment.

.3	Pressure test each completed system, in accordance with Section 23 08 43, before any equipment is started. Notify Minister [two] [   ] working days prior to any system pressure test.

.4	Boilers:  perform start-up and performance verification [using manufacturer’s representatives]. Provide [two] [   ] working days notice to the Minister.

.5	Chemically clean boilers in accordance with Section 23 25 19. Notify Minister [two] [   ] working days prior to any system cleaning.

.6	Chemically treat condensate return system in accordance with Section 23 25 19.

.7	Balance system in accordance with Section 23 08 83. Complete and submit Systems balance report to Minister.

.8	Check system for fluid or trap noise in pipes. Rectify as necessary.

.9	Complete and submit Steam systems Start-up report as specified in Section 23 08 13.

.10	Conduct Mechanical Equipment and Systems Demonstration and Instruction in accordance with Section 23 08 93.

3.5	CONTROL SYSTEMS

.1	Pressure test completed pneumatic system, in accordance with Section 23 08 43, before any equipment is started. Notify Minister [two] [   ] working days prior to system pressure test.

.2	Start-Up and performance test control air compressor and drier.

.3	Load Physical Point Data Base, start/stop schedules, alarms, run time logs, trend logs, etc. into EMCS control panels in accordance with Section 23 08 95.

.4	Commence [30] [   ] day trial use period by Minister.

.5	Perform EMCS Physical Point verification and calibration in accordance with Section 23 08 95.  Complete and submit Control Systems verification report to the Minister.

SPEC NOTE:  Include clause 3.5.6 if the custom control software is included in the Contract.

.6	Load and debug custom control software in accordance with Section 23 09 93.

.7	Calibrate pneumatic room thermostats.

.8	Provide Operator training at EMCS terminal in accordance with Section 23 09 23.

3.6	DOMESTIC WATER SYSTEMS

.1	Inspect domestic water systems including piping layout, pipe support, expansion  provisions, and slope for draining and venting, before  pressure testing any section of pipework. Notify Minister  when work is ready for inspection.

.2	Pressure test sections of pipework, in accordance with Section 23 08 43, prior to application of insulation or to concealment.

.3	Pressure test each completed system, in accordance with Section 23 08 43, before any equipment is started. Notify Minister [two] [   ] working days prior to any system pressure test.

.4	Start domestic hot water systems' circulator pumps.

.5	Domestic hot water heating appliance: perform start-up and performance verification [using manufacturer’s representative]. Provide [two] [   ] working days notice to the Minister.

.6	Balance Domestic Hot Water system return circulation circuits by temperature drop measurement.

.7	Sterilize Domestic water systems in accordance with Section 22 11 20. Notify Minister [two] [   ] working days prior to any system  sterilization.

.8	Ensure all air chambers and expansion compensators are properly installed.

.9	Ensure entire system can be completely drained.

.10	Check operation of water hammer arrestors. Let one outlet run for ten seconds, then shut water off quickly. If  water hammer occurs, replace water hammer arrestor. Repeat for each outlet and flush valve.

.11	Complete and submit Domestic Water systems Start-up report as specified in Section 23 08 13.

.12	Conduct Mechanical Equipment and Systems Demonstration and Instruction in accordance with Section 23 08 93.

3.7	PLUMBING DRAINAGE SYSTEMS

.1	Refer to Section 33 30 10 for inspection of Sewer Systems below ground, and Section 33 34 05 for pressure testing of Sanitary Sewage Force Mains.

.2	Inspect plumbing drainage systems including above ground drainage piping layout, pipe support, slope, venting, before pressure testing or concealing any section of the work. Notify Minister when work is ready for inspection.

.3	Hydraulically test above ground installations within buildings in accordance with Section 23 08 43. Notify Minister [two] [         ] working days prior to any system pressure test.

.4	Ensure all traps are fully primed.

.5	Ensure all fixtures are properly anchored and connected to system.

.6	Flush each valve, drain each sink and operate each fixture to ensure drainage and trap anti-siphon venting is effective.

.7	Open each cleanout, cover with linseed oil and reseal each cleanout. Ensure each cleanout is fully accessible and access doors are properly installed.

.8	Ensure roof drain metal domes are installed. Ensure storm piping is free of debris or roof insulation ballast. Remove caps as required. Verify insulation on piping is as specified in Section 20 20 30.

.9	In addition to pressure tests on chemical waste piping check the following:

.1	Chemical dilution [pit] [tank] installation.

.2	Manhole at street.

.3	Bottle traps properly installed and accessible.

.10	In addition to pressure tests check following on kitchen waste systems:

.1	Piping is installed to withstand 82°C discharge from dishwashers, boiler blowdown, etc.

.2	Grease trap is accessible and properly installed.

.11	Complete and submit Drainage systems Start-up report as specified in Section 23 08 13.

.12	Conduct Mechanical Equipment and Systems Demonstration and Instruction in accordance with Section 23 08 93.

3.8	STANDPIPE AND SPRINKLER SYSTEMS

.1	Inspect standpipe and sprinkler systems including piping layout, pipe support, slope for draining, before pressure testing any section of pipework.  Notify Minister when work is ready for inspection.

.2	Pressure test Standpipe and Sprinkler systems, in accordance with Section 23 08 43, before any equipment is started. Notify Minister [two] [   ] working days prior to any system pressure test.

.3	Ensure all equipment used has ULC labels visible.

.4	Start fire and jockey pumps as specified in Section 23 08 23.

.5	Ensure all valves in sprinkler system are monitored and are clearly visible.

.6	Ensure all flow switches are installed and are operational.

.7	Flush systems as follows:

.1	Fill with water, let stand at full operating pressure  for one week. Drain each riser separately, then drain  main.

.2	Repeat above procedure three times.

.8	Perform flow tests required by:

.1	Alberta Building Code.

.2	Authorities having jurisdiction.

.3	NFPA 13 - Standard for the Installation of Sprinkler Systems.

.4	NFPA 14 - Standards for the Installation of Standpipe and Hose Systems.

.5	NFPA 20 - Standards for the of Stationary Pumps for Fire Protection.

.9	Record incoming water pressure to building once a day for ten days prior to activating system.

.10	Adjust PRV on pump discharge to achieve maximum pressure of 620 kPa at top hose station. Adjust PRVs at lower hose stations to 550 kPa maximum.

.11	Test and place sprinkler valve into operation. Adjust pressure switches.

.12	Coordinate verification of fire alarm system with Division 26.

.13	Record flow and pump pressure for fire and jockey pumps  and inlet water pressure.

.14	Complete and submit Standpipe and Sprinkler systems Start-up report as specified in Section 23 08 13.

.15	Conduct Mechanical Equipment and Systems Demonstration and Instruction in accordance with Section 23 08 93.

END OF SECTION