Use this Section to specify Start-up and Testing for a computerized Energy Management Control System (EMCS) used to operate mechanical systems. The complete EMCS  is intended to be specified in a series of Sections.  Refer to Section 23 09 23 for a complete list of EMCS Sections.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Data Sheet - Reference Documents

.3	Specification Section Text:

1.	General

1.1	Intent

1.2	Related Sections

1.3	Start-Up Sheets

1.4	Documentation

2.	Products

Not Used

3.	Execution

3.1	Hardware

3.2	Point Check Out

3.3	Trial Use

3.4	Demonstration of System Integrity

3.5	Minister's Point Verification

3.6	Application Software

3.7	Demonstration of Application Software

3.8	User Control Software Implementation

3.9	Review of Deficiencies Before Interim Acceptance

Start-Up Sheets

.1	Physical Point Confirmation

.2	Analogue Output Device Range

.3	Flow Measuring Station Calibration

Samples of these facility start-up sheets are available from the Technical Services Branch, 3rd Floor, 6950 - 113 Street, Edmonton, Alberta.

END OF DATA SHEET

1.	General

1.1	INTENT

.1	Read this Section in conjunction with Section 23 09 23, EMCS General Requirements and other related EMCS Sections.

1.2	RELATED SECTIONS

.1	EMCS Field Sensing Devices and Actuators:	Section 23 09 29.

.2	EMCS Control Sequences:	Section 23 09 93.

1.3	START-UP SHEETS

.1	Provide “Physical Point Confirmation” sheets as follows:

.1	Basic form of sheets shall follow ordering and layout of point sheets in section 230930.  Provide sample for review prior to commencement of Start-up checks.

.2	Include the following information/fields:

.1	System description and mnemonic

.2	Point description and mnemonic

.3	RCU number or identifier

.4	Point Type and Specified accuracy

.5	Tagged (tick box indicating presence of properly affixed identification tag/s)

.6	Verified (tick box indicating successful end-to-end wiring check)

.7	EMCS displayed value

.8	Field measured value

.9	Calibration offset value

.10	Identifier/name of graphic containing EMCS displayed value

.11	Contractor’s initials

.12	Verifier’s initials (Minister’s Representative)

.13	Remarks

.2	Provide “Analogue Output Device Range” sheets as follows:

.1	These sheets are to be used in addition to the Physical Point Confirmation sheets and shall include all EMCS analogue output devices.  Order of devices shall follow ordering of analogue outputs as found on the Physical Point Confirmation sheets.  Provide sample for review prior to commencement of Start-up checks.

.2	Include the following information/fields:

.1	System description and mnemonic

.2	Point description and mnemonic

.3	RCU number or identifier

.4	Specified range

.5	FCE state at EMCS output value of 0% of range

.6	FCE state at EMCS output value of 20% of range

.7	FCE state at EMCS output value of 80% of range

.8	FCE state at EMCS output value of 100% of range

.9	FCE state at EMCS output value of 80% of range

.10	FCE state at EMCS output value of 20% of range

.11	FCE state at EMCS output value of 0% of range

.12	Actual range of device

.13	Verified FCE end-of-travel @ 0% (tick box indicating successful check)

.14	Verified FCE end-of-travel @ 100% (tick box indicating successful check)

.15	Failsafe position (NO/NC, OFF/ON, etc.)

.16	Verified (tick box indicating successful failsafe check)

.17	Contractor’s initials

.18	Verifier’s initials (Minister’s Representative)

.19	Remarks

NOTE 1:	FCE state refers to the position or value of the Final Control Element affected by the analogue output.  Examples:  damper or valve position, fan speed, setpoint reset value, etc.

NOTE 2:	FCE end-of-travel refers to the end condition achieved by the FCE.  Examples:  dampers/valves achieve full open or tight shut off, fan achieves specified min/max speed, setpoint achieves specified max/min reset value, etc

.3	Provide “Flow Measuring Station Calibration” sheets as follows:

.1	These sheets are to be used in addition to the Physical Point Confirmation sheets and shall include all EMCS analogue input devices used for flow rate measurement.  Provide a sheet for each station.  Sort sheets to follow ordering of these inputs as found on the Physical Point Confirmation sheets.  For each flow station type, provide sample for review prior to commencement of Start-up checks.

.2	Include the following information/fields:

.1	System description and mnemonic

.2	Point description and mnemonic

.3	RCU number or identifier

.4	Type, make, model and serial number of each measuring instrument used

.5	Flow station type, make, model, size and serial number if available

.6	Transducer:

-  type,  make and model

- operating range

- serial number if available

- zeroed (tick box indicating device was checked for proper zero reading)

.7	Start and stop times of measurement sequence

.8	Media (air, water, glycol) temperature

.3	For Air-Flow Stations:  Provide fields to record traverses according to recommendations of the 2005 A.S.H.R.A.E. Fundamentals Handbook (SI version), chapter 14 "Measurement and Instruments", page 14.17 “Measuring Flow in Ducts”.  Use the Log-Tchebycheff Rule dimensions, for both rectangular and round ducts as given in Figure 7 on page 14.18.  Include field to record atmospheric barometric pressure at time of testing.

.4	For Fluid-Flow Stations:  Provide fields to record data according to the station manufacturer’s recommended calibration procedures.  Include fields to record fluid type, density and application.

.5	Provide space for performing required calculations.  Include all flow calculation formula used as well as fields for correction factors applied.

.6	Include fields to record EMCS trend data and the calculations used in determining the average of the displayed flow rates over the duration of the tests.

.7	Provide a summary area for the calculation of a flow station calibration equation that will be entered into the EMCS database or via programming.

.4	All values and calculations shall be in MKS (metric) units.

1.4	DOCUMENTATION

.1	Submit complete system documentation before start of testing, including:

.1	programmer's instruction manuals.

.2	CCU operating system software manuals and original diskettes.

.3	application software program manuals and original diskettes.

.4	operating manuals for terminals and end devices.

.5	interlock and control schematics for each system controlled, identifying each EMCS physical point by mnemonic.

.6	table of operating set points and alarm limits for each system.

.7	device calibration methods and procedures.

.8	list of all real and virtual mnemonics, with full English description of each mnemonic.

.9	well documented User Control Language software with comment lines to explain control strategies.  Alternatively, written description of control strategy for each software module.

.10	backup disks for User Control Language Software.

2.	Products

Not Used

3.	Execution

3.1	HARDWARE

.1	Verify that each hardware component has been properly installed as recommended by manufacturer and is functioning correctly.

.2	Verify that all circuits are complete and all terminal wiring connections are tight.

.3	Electronic hardware:

.1	Start-up electronic hardware as recommended by manufacturer.

.2	Replace defective components.

.3	Prove proper operation, use software diagnostic.

.4	Interfaces:

.1	Test to ensure interfaces with Division 25 and 26 and other control packages are complete.

.2	Verify that interface cabinets comply with applicable codes and specified requirements.

.5	Check operation of system under failure modes:

.1	Power failure.

.2	RCU failure.

.3	Network failure.

.4	Sensor failure.

3.2	POINT CHECK OUT

.1	Verify point mnemonic, hardware address, correct physical location and proper functioning of each hardware point on system.  Record verification of each point on “Physical Point Confirmation” sheets.

.2	Calibrate all analogue input/output devices, actuators, transducers and sensors as recommended by manufacturer.

.3 	Achieve end-to-end (between field device and actual value displayed on screen) calibration accuracy over full expected operating range as specified for each analogue point type in Section 23 09 29:

.1   	Calibration may be performed on the hardware device if this feature is available, or may be entered into database/software provided correction is not greater than five (5) times specified accuracy for device.  Device must be replaced and calibrated again if correction is outside this band.  Combination coarse hardware and fine database/software calibration is allowed.

.2	Simple offset calibration is acceptable where the operating range is less than 25% of the device span.  Slope calibration is required for devices operating over larger spans.  A two-point slope calibration, where the samples are about 20% from each end of the operating range is acceptable if the resulting offset at the middle of the operating range falls within the specified accuracy.

.2	All database/software calibrations must be entered even if these fall within the specified accuracy.

.3  	Document each calibration correction on "Physical Point Confirmation" Sheets.

.4	Check range and repeatability of each analogue output point.  Ensure tight shut-off of dampers and valves.

SPEC NOTE:  Include the following article for retrofit contracts when pneumatic actuators are to be retained or added.

.6	Calibrate all control valve, damper actuators and positioners. Hysteresis shall not be greater than 5% of range. Ensure:

.1	No overlap of control spring ranges.

.2	No leakage when device is closed.

.3	Fail-safe operation.

SPEC NOTE:  Include the following article when Variable Air Volume Systems with Air Flow Measuring Stations are specified.

.7	Variable Air Volume systems with Air Flow Measuring stations:

.1	Statically adjust each pressure transducer to zero with both ports at ambient pressure.  Check each transducer’s span for linearity and range using an inclined manometer or a Shortridge Air Data Multi-meter in parallel with the transducer.

.2	Dynamically calibrate each Air Flow Measuring station using the procedure defined on “Flow Measuring Station Calibration” sheets.  Document the results on “Flow Measuring Station Calibration” sheets.  For air systems flowing less than 5000 l/s, it is acceptable to use two calibration points at 60% and 85% vane/speed position.  For small air systems flowing less than 2000 l/s, it is acceptable to use a single calibration point at 75% vane/speed position.

.3	If, at any flow setting, the EMCS displayed flow rate differs by more than 5% from the measured flow rate, add an air flow measuring station calibration correction  equation to the controls software or point database.  The equation must go through the origin.  Any zero offset usually corresponds to an improper zeroing of the velocity pressure transducer.  A linear equation that provides a simple slope correction to achieve final accuracy to better than 5% is preferred.

.8	Dial-out Alarm and Watch-Dog Timer

.1	Verify watch-dog timer operation by creating a power fail condition in the controller containing the watch-dog timer output point.

.2	Verify end to end operation of each dial out alarm by creating an alarm condition for each alarm as specified under 23 09 93 “Critical Dial-out Alarms”.

3.3	TRIAL USE

SPEC NOTE:  Edit the number of days specified in items 3.3.1 and 3.3.3 to reflect the requirements for the project.  As a guideline allow (1 + (# points / 40) as the number of days for 3.3.3  if  contractor assistance is required to commission the EMCS.

.1	[Fifteen] days before Interim Acceptance of the Work provide the Minister with full access to EMCS for Minister's trial use of system.

.2	Trial use is to determine EMCS's compliance with Specifications, and to permit Minister to verify installation and accuracy of calibration of all physical points connected to EMCS.

.3	Provide a qualified EMCS representative for [five] days on-site to assist with the Minister's trial use of system.  NOTE:  Contractor correction and repair of deficiencies does not constitute verification.  Time taken for this corrective work shall not be counted towards the specified period of on site assistance.

3.4	DEMONSTRATION OF SYSTEM INTEGRITY

.1	Prior to Interim Acceptance of the Work, demonstrate the following EMCS features to Minister:

.1	Power fail and restart of CCU, RCU, TCU

.2	Network failure and restart

.3	Sensor failure and recovery in RCU and TCU

.4	Fail-safe modes for all valves, dampers and equipment.

.5	Fail-safe and emergency modes for systems.

.2	Prior to Interim Acceptance of the Work, demonstrate to the Minister all control sequences for equipment not directly controlled by EMCS, including component hard wired interlocks.

3.5	MINISTER'S POINT VERIFICATION

.1	The Minister will verify all EMCS physical points for correct connection, calibration and operation after Contractor prepared “Physical Point Confirmation” sheets have been reviewed by the Minister.

.2	The Minister's point verification will be carried out during the Minister's trial usage of the system.

.3	All required trend logs and screen graphics shall be complete and fully functional prior to Minister’s Point Verification.

3.6	APPLICATION SOFTWARE

.1	Ensure all hardware is installed and started and fully operational before software start-up.

.2	Enter each physical point into database and include following:

.1	Set up run time capture for each digital output.

.2	Enter engineering units for each analogue point.

.3	Set up an alarm point for each digital input/output pair, with delay before alarm is enunciated.

.4	Set up an alarm point for each analogue input with high and low limits.  Provide a reset differential.

.5	Enter physical point calibration corrections.

.6	Enter analogue input conversion equations for fluid velocity measuring devices.

.3	Enter start/stop schedules for all systems not required to run continuously.

.4	Trend Logs:

.1	Enter trend logs for each physical analogue input and output point in EMCS database.

.2	Trend logs shall retain a minimum of four readings per hour for 24 hours.

.3	Trend logs shall be continuous and shall overwrite information that is 24 hours old.

.4	Provide an additional trend log of 120, ten second interval, readings for each P.I.D. loop  controlling and controlled variable.

.5	Grouping of trend log points on print outs shall be agreed with the Minister.

SPEC NOTE:  Include the following article if dynamic graphics are part of EMCS.

.5	Verify proper operation of dynamic graphics:

.1	Proper identification of system and points on screen.

.2	Data refresh period.

.3	Dynamic valve/damper actuators displayed on screen.

.4	Colour change on status change.

.5	Reaction to alarms.

.6	Trend graph reporting.

3.7	DEMONSTRATION OF APPLICATION SOFTWARE

.1	Demonstrate following to the Minister:

.1	Man/machine interface to EMCS system, including operator access, all monitoring functions and command of points.

.2	Saving and reloading of database.  Provide a checklist describing the procedures to be followed.

.3	The use of disk backup utilities by creating bootable CDs containing a complete image backup of the hard disk.  Save must be performed at the highest rewrite speed available on CD-RW drive.  Provide a checklist describing the procedures to be followed.

.4	User Control Language program entry and editing.

.5	Operation of specific application software such as:

.1	demand limiting.

.2	peak shaving.

.3	night setback.

.4	optimum start of heating/cooling systems.

.5	building dynamic control.

.6	alarm conditions and printouts.

.7	automatic report generation.

3.8	USER CONTROL SOFTWARE IMPLEMENTATION

.1	Demonstrate User Control Language software operation, start up and shut down sequences, software interlocks, fail safe, emergency shut down and alarm condition control strategies in accordance with the requirements of Section 23 09 93.

3.9	REVIEW OF DEFICIENCIES BEFORE INTERIM ACCEPTANCE

.1	Review all deficiencies and agree upon a deficiency list with the Minister, before Interim Acceptance of the Work.

## END OF SECTION