Section Cover Page

Section 23 25 00 Cleaning and Chemical Treatment 2008-05-01 of Piped Systems

Use this Section to specify the chemical cleaning and treatment of hydronic systems and domestic water systems. Refer to Sections 22 11 20, 23 25 01,23 25 02 and 23 25 13 of the Basic Master Specification (BMS) for a complete list of sections related to Chemical Cleaning and Treatment of Mechanical Systems.

Include Chemical Treatment or Softening of the domestic water system Section 22 11 20, BMS, only when required by the Lodge Foundation.

This Master Specification Section contains:

.1	This Cover Page

.2	Data Sheet - Guidelines for Renovated Systems

.3	Specification Section Text:

1.	General

1.1	Intent

1.2	Related Sections

1.3	Performance Requirements

1.4	Submittals

1.5	Detail Drawings

1.6	Spare Parts and Maintenance Materials

1.7	Quality Assurance

1.8	Instruction

  - Sequencing

2.	Products

2.1	Cleaning Chemicals

2.2	Chemical Treatment Materials

2.3	Miscellaneous Materials

2.4	Water Test Equipment

2.5	Equipment and Materials

3.	Execution

3.1	Equipment Installation

3.2	Cleaning - General

3.3	Cleaning Procedure

3.4	Deposit Removal Procedure

3.5	Chemical Treatment - Control Limits

3.6	Operation Maintenance until Interim Acceptance

3.7	Chemical Cleaning and Treatment Schedule for Renovated Systems

3.8	Disposal of Spent Cleaning Solution

3.9	Equipment Installation

3.10	Chemical Treatment and Cleaning Equipment Schedule

.4	Detail Drawings:

23 25 00.01	Chemical Pot Feeder

23 25 00.02	Installation of Chemical Pot Feeder, By-pass Filter

1.	When any of the following work has been performed, no cleaning is required but loose deposits must be flushed out before flooding with system water.

.1	A minor amount of new piping is added to the system when compared with the entire system.

.2	Fin-tube boiler is re-tubed.

.3	Less than approximately 50% of the tubes are replaced in a fire-tube boiler.

2.	New piping which can be isolated from the rest of the system:

.1	Clean piping using chemical cleaner and procedure specified in 2.1.1 and 3.3.

.2	Chemically treat the entire system with corrosion inhibitor specified in 2.2 and 3.5.

3.	New piping which cannot be isolated from the rest of the system:

.1	Clean deposits from the entire system as specified in 2.1.2 and 3.4.

.2	Clean the entire system with chemical cleaner and procedure specified in 2.1.1 and 3.3.

.3	Chemically treat the entire system with corrosion inhibitor specified in 2.2 and 3.5.

4.	Removal of deposits from system/boiler where no new piping is added or re-tubing is done:

.1	Clean deposits from the system/boiler as specified in 2.1.2 and 3.4.

.2	Chemically treat the system/boiler with a corrosion inhibitor specified in 2.2 and 3.5.

1.	General

1.1	INTENT

.1	This Section specifies services and material required for on site cleaning and chemical treatment of a multi-metal, closed loop [hot water heating system][and][hot and cold domestic water system].

1.2	RELATED SECTIONS

.1	Mechanical Operations and Maintenance Manuals	Section 20 01 06.

.2	Tanks	Section 20 15 00.

1.3	PERFORMANCE REQUIREMENTS

.1	Clean hydronic system to remove oil, grease, silt, and rust and leave metal surfaces well passivated.

.2	Chemically treat and maintain hydronic system water to meet following standards:

Parameter	Control Limits

Suspended solids:	Nil.

Iron Corrosion Rate:	stable rate, 0.5 mils per year

maximum, no pitting.

Copper Corrosion Rate:	stable rate, 0.2 mils per year

maximum, no pitting.

Total Iron Concentration:	0.5 mg/L Fe maximum.

Total Copper Concentration:	0.2 mg/L Cu maximum.

Total Plate Count	103 organisms/mL maximum.

1.4	SUBMITTALS

.1	Submit a written report of actual cleaning activities including:

.1	Times.

.2	System status.

.3	Problems encountered.

.4	Actions taken.

.5	Composition of cleaning & spent cleaning solutions.

.6	Inspection results.

.7	Final concentration of corrosion inhibitor in hydronic system.

.8	corrosion rates in hydronic systems.

.9	Final suspended solids concentration in system.

.10	Final iron concentration in systems.

.11	Final copper concentration is system.

.12	Description of site preparatory work required by the minister.

.13	Proposed cleaning procedure.

.14	Material and safety data sheets for all treatment  materials.

.15	Method of disposal of solutions.

1.5	DETAIL DRAWINGS

.1	Following detail drawings form part of this Section:

.1	23 25 00.01	Chemical Pot Feeder.

.2	23 25 00.02	Installation of Chemical Pot Feeder, By-pass Filter.

1.6	QUALITY ASSURANCE

.1	Use a qualified water treatment specialist, who has a demonstrated record of expertise in water systems cleaning and chemical treatment, to supply chemicals, equipment, and consulting services to perform cleaning and chemical treatment work specified.

.2	Provide documentation from an accredited independent laboratory if requested by the minister.

.3	Deliver inhibitor chemicals to the site in sealed and labelled containers.

1.7	INSTRUCTION

.1	Provide operation and maintenance instructions for water treatment systems including following:

.1	Chemical requirements for water treatment.

.2	Water test procedures.

.3	Operation and maintenance of water treatment equipment.

1.8	SEQUENCING

.1	Perform cleaning and chemical treatment activities as one continuous process without interruption.

2.	Products

SPEC NOTE:  Inside surfaces of hot water heating systems components must not be galvanized.

2.1	CLEANING CHEMICALS

.1	Cleaning Solution: neutral pH cleaning solution which is capable of removing oil, grease, and rust from metal surfaces of system and passivating cleaned metal surfaces of system.  Cleaning solution shall include:

.1	Low foaming non-ionic surfactant for penetrating oily and greasy deposit surfaces.

.2	Solvent for dissolving oil and grease.

.3	Dispersant for dissolving rust.

.4	Reducing agent for corrosion control.

.5	Ferrous and non-ferrous metal corrosion inhibitors.

SPEC NOTE:  Specify deposit removal cleaning solution for existing systems.

.2	Deposit Removal Cleaning Solution: blended neutral pH cleaning solution which is capable of removing scale and iron deposits, destroying bacteria, and passivating the metal surfaces of system.

2.2	CHEMICAL TREATMENT MATERIALS

SPEC NOTE:  Select a corrosion inhibitor using the following guidelines:

-  New Systems:  use molybdate based corrosion inhibitor unless specific project requirements dictate otherwise.

-  Existing Systems:  corrosion inhibitor must be compatible with the existing corrosion inhibitor.

.1	Corrosion Inhibitor:  containing following:

.1	[Molybdate] [Sulphite] [Nitrite] based materials for corrosion protection of ferrous material in system.

.2	Azole for corrosion protection of non-ferrous material.

.3	Buffer for pH level control.

2.3	MISCELLANEOUS MATERIALS

.1	By-pass Filter Cartridge:  sting-wound replacement filter cartridges, sized for retention of particles greater than 20 microns in diameter.

2.4	WATER TEST EQUIPMENT

.1	Supply one of each of the following water test kits:

.1	pH test kit.

.2	Corrosion inhibitor test kit.

.3	TDS (Total Dissolved Solids) or Conductivity Meter.

2.5	EQUIPMENT AND MATERIALS

.1	Chemical Pot Feeder:  capable of operating at system working temperature and pressure.  As detailed on drawing 23 25 00.01, appended to this Section.

.2	By-pass Filter:  constructed of steel, sized to handle 5% of system circulating rate, and capable of operating at system working temperature and pressure.  As detailed on drawing 23 25 00.02, appended to this Section.

.3	In-line Flow Restriction Device:  constructed of steel and glass, sized to control flow through by-pass filter at an adjustable rate of 0-0.63 L/S, and capable of operating at system working temperature and pressure.

3.	Execution

3.1	EQUIPMENT INSTALLATION

.1	Prior to performing chemical treatment work ensure following work has been completed:

.1	Chemical pot feeder.

.2	By-pass filter and in-line flow restriction device.

3.2	CLEANING - GENERAL

.1	Maintain following conditions during cleaning process:

.1	Manual and automatic valves are in full open position.

.2	By-pass valves are operated to ensure full flow through entire system.

.3	Safety devices, including pressure relief valves, flow switches, and pressure switches are functioning.

.4	System is operated with a minimum pressure of 35 kPa(g) at highest point and expansion tank level is maintained at 1/3 to 1/2 full of water.

.5	Temporary fine mesh strainers for system pump and control valve strainer baskets are installed and cleaned as required.

.6	Completely flush domestic water system to remove debris and solder slag.  Test water for potability and continue to flush until acceptable condition are obtained throughout the system.

3.3	CLEANING PROCEDURE

.1	Step 1:  Fill system with domestic water, establish circulation, and heat system contents to a temperature of 60oC.

.2	Step 2:  After two hours of circulation, collect water samples from at least three different locations in system.  If these samples contain suspended solids, clean out strainer baskets, drain system, and repeat steps 1 & 2.

.3	Step 3:  Blend in prepared concentrated cleaning solution, establish circulation, and maintain system temperature at 60°C for at least three days.

.4	Step 4:  Dump spent cleaning solution to disposal, fill system with domestic water, circulate system contents for at least two hours, and dump spent rinse water to disposal.

.5	Step 5:  Fill system with domestic water and repeat step 4 until water samples collected from system are free of oil, grease, and suspended solids.

.6	Step 6:  Drain system completely, including all system low points and perform visual inspections of metal surfaces at three different locations.

.7	Complete steps 4, 5 & 6 within a 24 hour period.

.8	If metal surfaces contain oil/grease or silt, fill the system with domestic water and repeat steps 3, 4, 5 & 6.

.9	Immediately after inspection is completed, install filter cartridge and operating pump, fill system with domestic water, blend in concentrated corrosion inhibitor solution until its concentration in system is at an acceptable level for film formation, and pass system water through by-pass filter and corrosion coupon rack.

SPEC NOTE:  Specify deposit removal procedure for cleaning of existing systems.

3.4	DEPOSIT REMOVAL PROCEDURE

.1	Step 1:  Fill system with domestic water, establish circulation, and heat system contents to a temperature of 60oC;

.2	Step 2:  Blend in prepared concentrated cleaning solution for removal of deposits etc., establish circulation, and maintain system temperature at 60oC until total iron concentration stabilizes;

.3	Step 3:  Dump spent cleaning solution to disposal, fill system with domestic water, circulate system contents for at least two hours, and drain spent rinse water from various locations in system to disposal;

.4	Step 4:  Fill system with domestic water and repeat step 3 until water samples collected from system are free of suspended material;

.5	Step 5:  Drain system and perform visual inspections of metal surfaces at three different locations;

.6	Complete steps 3, 4, & 5 within a 24 hour period.

.7	Step 6:  If metal surfaces contain scale or iron deposits and are not passivated, fill system with domestic water and repeat steps 2, 3, 4 & 5.

3.5	CHEMICAL TREATMENT - CONTROL LIMITS

.1	For first month after chemical treatment maintain primary control limits at upper limits to promote film formation.

.2	Maintain following control limits for inhibitor used in system until Interim Acceptance of the Work:

| Inhibitor | Primary Control Limits | Secondary Control Limits |
| --- | --- | --- |
| SPEC NOTE: Specify only the inhibitor which is specified in Clause 2.1.2. |
| Molybdate | 50-100 mg/L Mo | 9.0-10.0 pH |
|  |  | 2000 mg/L TDS max or |
|  |  | 2500 micromhos/cm max |
| Sulphite | 50-100 mg/L SO3 | 8.5-9.5 pH |
|  |  | 2000 mg/L TDS max or |
|  |  | 2500 micromhos/cm max |
| Nitrite | 700-1500 mg/L NaNO2 | 9.0-10.0 pH |
|  |  | 3000 mg/L TDS max or |
|  |  | 3500 micromhos/cm max |

3.6	OPERATION MAINTENANCE UNTIL INTERIM ACCEPTANCE

.1	Perform following minimum routine maintenance until Interim Acceptance of the Work:

.1	Maintain control limits specified under “Performance Requirements” and “Chemical Treatment - Control Limits”. Add chemicals as required.

.2	Replace fouled filter cartridges in by-pass filter with new filter cartridges as required to maintain continuous flow through filter.

.3	Test system to confirm that adequate treatment is in the system.

.2	Document water analyses results, quantities, dates chemicals added and make-up water used on chemical treatment report form.

3.7	CHEMICAL CLEANING AND TREATMENT SCHEDULE FOR RENOVATED SYSTEMS

SPEC NOTE:  Schedule cleaning requirements for renovated hydronic systems based on the guidelines on Page 01.

.1	Clean and treat renovated hydronic systems as follows:

.1	New piping - isolated from rest of system:

.1	Chemically clean piping.

.2	Chemically treat entire system with corrosion inhibitor.

.2	[                                             ]:

.1	[                                             ].

.2	[                                             ].

.3	[                                             ].

3.8	DISPOSAL OF SPENT CLEANING SOLUTION

.1	Dispose of spent cleaning solution in an environmentally responsible manner.  Following methods are acceptable:

.1	Disposal through sanitary sewer if regulatory body will accept spent cleaning solutions and issue a disposal permit.

.2	Disposal at an off-site disposal facility which meet Alberta Environment requirements.

3.9	EQUIPMENT INSTALLATION

.1	Install chemical pot feeder in accordance with detail drawing appended to this Section.

.2	Install by-pass filter in accordance with detail drawing, appended to this Section.  Do not install filter cartridge until system has been cleaned.

3.10	CHEMICAL TREATMENT AND CLEANING EQUIPMENT SCHEDULE

.1	Supply and install chemical treatment and cleaning equipment for systems as follows:

| System | Equipment |
| --- | --- |
| Hydronic Systems | Chemical Pot Feeder By-Pass Filter By-Pass Filter Cartridge In-line Flow Restriction Device- |

END OF SECTION