Section Cover Page

Section 23 25 01 Cleaning and Chemical Treatment 2013-04-04 Equipment

Use this Section to specify the equipment required for chemical treatment and cleaning mechanical systems.  Refer to Section 23 25 02 for a complete list of other sections related to Chemical Cleaning and Treatment of Mechanical Systems.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Data Sheet - Reference Standards

.3	Specification Section Text:

1.	General

1.1	Intent

1.2	Related Requirements

1.3	Detail Drawings

1.4	Reference Documents

1.5	Product Data

1.6	Spare Parts and Maintenance Materials

2.	Products

2.1	Equipment and Materials

3.	Execution

  - Equipment Installation

  - Waste Water and Material Disposal

3.3	Chemical Treatment and Cleaning Equipment Schedule

.4	Detail Drawings:

23 25 01.01	Chemical Pot Feeder and Corrosion Coupon Rack

23 25 01.02	Installation of Chemical Pot Feeder, By-pass Filter, Corrosion Coupon Rack, and Sample Cooler

23 25 01.03	Installation of Chemical Metering System for Steam Boilers

23 25 01.04	Installation of Corrosion Coupon Rack, Chemical Metering System and Total Dissolved Solids Control System, for Condenser Water System

23 25 01.05	Installation of Corrosion Coupon Rack, Chemical Metering System and Total Dissolved Solids Control System, for Evaporative Condenser Water System

23 25 01.06	Packaged Steam Humidification System

1.	General

1.1	INTENT

.1	This Section specifies equipment which needs to be installed as part of mechanical systems to permit chemical cleaning, chemical treatment and monitoring to be performed.

1.2	RELATED Requirements

.1	Spare Parts and Maintenance Materials:	Section 20 00 23.

.2	Mechanical Operation and Maintenance Data:	Section 20 01 05.

OR

.2	Mechanical Operations and Maintenance Manuals:	Section 20 01 06.

.3	Chemical Treatment and Cleaning - General Requirements:	Section 23 25 02.

.4	Cleaning and Chemical Treatment of Hydronic Systems:	Section 23 25 13.

.5	Cleaning and Chemical Treatment of Steam Boiler Systems:	Section 23 25 19.

.6	Cleaning and Chemical Treatment of Condenser Water Systems:	Section 23 25 20.

.7	Cleaning and Chemical Treatment of Glycol Systems:	Section 23 25 26.

.8	Cleaning and Chemical Treatment of Spa/Swimming Pools:	Section 25 51 19.

1.3	DETAIL DRAWINGS

.1	Following detail drawings form part of this Section:

.1	23 25 01.01	Chemical Pot Feeder and Corrosion Coupon Rack

.2	23 25 01.02	Installation of Chemical Pot Feeder, By-pass Filter, Corrosion Coupon Rack, and Sample Cooler.

.3	23 25 01.03	Installation of Chemical Metering System for Steam Boilers.

.4	23 25 01.04	Installation of Corrosion Coupon Rack, Chemical Metering System and Total Dissolved Solids Control System, for Condenser Water System.

.5	23 25 01.05	Installation of Corrosion Coupon Rack, Chemical Metering System and Total Dissolved Solids Control System, for Evaporative Condenser Water System.

.6	23 25 01.06	Packaged Steam Humidification System

1.4	REFERENCE DOCUMENTS

.1	American Society for Testing and Materials (ASTM):

| .1 | ASTM D2688-05 | Standard Test Methods for Corrosivity of Water in the Absence of Heat Transfer (Weight Loss Methods) |
| --- | --- | --- |

1.5	PRODUCT DATA

.1	Comply with requirements of Division 01.

.2	Provide product data for each piece of equipment and control systems.  Include sizes and capacity for each system.

1.6	SPARE PARTS AND MAINTENANCE MATERIALS

.1	Provide spare parts and maintenance materials specified in Section 20 00 23 and this Section.

2.	Products

2.1	EQUIPMENT AND MATERIALS

.1	Sample Cooler: to ASTM D1192, capable of operating at system working temperature and pressure.

.2	Chemical Pot Feeder: as detailed on Detail 23 25 01.01, capable of operating at system working temperature and pressure.

.3	Corrosion Coupon Holders: fabricated in accordance with ASTM D2688.  Two for each system.

.4	Corrosion Coupon Rack: as detailed on Detail 23 25 01.02.  One for each system.

.5	Corrosion Coupons: supplied and installed by the Minister.

.6	By-pass Filter: constructed of steel, sized to handle 5% of system circulating rate, and capable of operating at system working temperature and pressure.  As detailed on Detail 23 25 01.02

.7	Flow Indicator: constructed of bronze and glass, with ball, sized to handle 5% of system circulation rate, and capable of operating at system working temperature and pressure.

.8	In-line Filter: constructed of steel or fibreglass, sized to handle 100% of system circulating rate, with valve structure to permit backwash, rinse, by-pass & service operation, and capable of operating at system working pressure and temperature.

.9	Blowdown Tank: to ASME VIII, capable of operating at system working temperature and pressure.

.10	Chemical Metering System: consisting of:

.1	Chemical Feed Pump: positive displacement type chemical feed pump, with adjustable settings for stroke length and stroke frequency, built-in check and relief valves, foot valves, and PVC suction and discharge tubing, capable of producing a higher pressure than system pressure.

.2	Chemical Mixing Tank Assembly: with 189 L high density free standing moulded polyethylene tank with a split removable cover, a pump shelf mount above or to the side of the tank, and agitator bracket.

.3	Agitator: electrical motor driven agitator, complete with sealed motor, stainless steel shaft and propeller.

.11	Softener System: consisting of:

.1	Two fibreglass reinforced plastic vessels, each sized for 100% make-up requirements.

.2	Controller for automatic regeneration and manual regeneration initiation.  Automatic feature to initiate regeneration based on adjustable totalized quantity of softener feed water, to prevent simultaneous regenerations, and to permit time adjustment for backwash, brine and rinse steps.

.3	Full charge of capacity exchange resin which has a capacity of 68.8 kg/m3 of resin at a regeneration salt dosage level of 240 kg/m3 of resin.

.4	High density polyethylene brine tank, sized to contain equivalent amount of salt required for ten regenerations, plastic valves, and PVC tubing.

.5	Softener inlet water meter, calibrated in m3.

.12	Total Dissolved Solids Control System: consisting of following:

.1	Total dissolved solids controller with adjustable set-point.

.2	Total dissolved solids sensing equipment.

.3	Solenoid operated bleed valve.

3.	Execution

3.1	EQUIPMENT INSTALLATION

.1	Install sample cooler for heating systems in accordance with ASTM D1192 and Detail 23 25 01.02

.2	Install chemical pot feeder in accordance with Detail 23 25 01.01 and 23 25 01.02.

.3	Install by-pass filter in accordance with Detail 23 25 01.02.  Do not install filter cartridge until system has been cleaned.

.4	Install corrosion coupon rack in accordance with Detail 23 25 01.01  and 23 25 01.02.

.5	Coupons will be installed by the Minister:

.1	After system has been cleaned.

.2	After system(s) are fully operational and treated.

.6	Install in-line filter downstream of circulating pump.  Make connections to direct filter backwash and rinse water to drain.

.7	Install chemical metering system in accordance with Detail [23 25 01.03] [23 25 01.04] [and] [23 25 01.05].

.8	Install total dissolved solids control system in accordance with Detail [23 25 01.04] [23 25 01.05].

.9	Install blowdown tank and sample cooler for steam systems in accordance with 23 25 01.03 and 23 25 01.06.  Pipe softened cold water to equipment for discharge temperature and scale control.

3.2	Waste Water and Material Disposal

.1	Dispose of waste water and materials in accordance with the “Alberta Infrastructure Water Treatment Program Manual, Section I - Environmental Guideline”.

3.3	CHEMICAL TREATMENT AND CLEANING EQUIPMENT SCHEDULE

.1	Supply and install chemical treatment and cleaning equipment for systems as follows:

| System | Equipment |
| --- | --- |
| Hydronic Systems | Sample Cooler (for heating systems only) |
| Section 23 25 13 | Chemical Pot Feeder |
|  | Corrosion Coupon Holders |
|  | Corrosion Coupon Rack |
|  | By-pass Filter |
|  | By-pass Filter Cartridge |
|  | Flow Indicator |
| Steam Boiler Section 23 25 19 | Sample Cooler Blowdown Tank |
|  | Chemical Metering System See Note (1) |
|  | Softener System |
| Condenser System | Total Dissolved Solids Control System |
| Section 23 25 20 | Corrosion Coupon Holder |
|  | Corrosion Coupon Rack |
|  | Chemical Metering System |
| Glycol System | Sample Cooler (for heating systems only) |
| Section 23 25 26 | Corrosion Coupon Holders |
|  | Corrosion Coupon Rack |
|  | By-pass Filter |
|  | By-pass Filter Cartridge |
|  | Flow Indicator |
| Spa/Swimming Pools | Chemical Metering System |
| Section 22 51 19 | In-Line Filter |

Notes:

(1)	If the steam boiler system contains a deaerator, two duplicate chemical feed systems are required, one for the addition of sulphite to the storage section of the deaerator  and one for the addition of chemical treatment to the steam boiler drum.

END OF SECTION