Section Cover Page

Section 23 25 20 Cleaning and Chemical Treatment 2012-11-09 of Condenser Water Systems

Use this Section to specify the chemical cleaning and treatment of condenser water systems.  Refer to Section 23 25 02 for a complete list of sections related to Chemical Cleaning and Treatment of Mechanical Systems.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Data Sheet – Reference Standards

.3	Data Sheet - Guidelines for Renovated Systems

.4	Specification Section Text:

1.	General

1.1	Intent

1.2	Related Requirements

1.3	Reference Documents

1.4	Performance Requirements

1.5	Submittals

2.	Products

2.1	Cleaning Chemicals

2.2	Chemical Treatment Materials

2.3	Corrosion Coupons

2.4	Water Test Equipment

3.	Execution

3.1	Equipment Installation

3.2	Cleaning - General

3.3	Cleaning Procedure

3.4	Deposit Removal Procedure

  - Operation Maintenance until Interim Acceptance.

  - Waste Water Disposal

3.7	Chemical Cleaning and Treatment Schedule for Renovated Systems

1.	When any of the following work has been performed, no cleaning is required but loose deposits must be flushed out before flooding with system water.

.1	A minor amount of new piping is added to the system when compared with the entire system.

.2	Chiller is re-tubed.

.3	Cooling tower is re-built.

2.	New piping which can be isolated from the rest of the system:

.1	Clean piping using the chemical cleaner and procedure specified in 2.1.1 and 3.3.

.2	Chemically treat the entire system with corrosion and scale inhibitor and biocide specified in 2.2 and 3.5.

3.	New piping which can not be isolated from the rest of the system:

.1	Clean the deposits from the entire condenser water system as specified in 2.1.2 and 3.4.

.2	Clean the entire system with the chemical cleaner and procedure specified in 2.1.1 and 3.3.

.3	Chemically treat the entire system with a corrosion and scale inhibitor and biocide specified in 2.1.2 and 3.5.

4.	Removal of deposits from system where no new piping is added or re-tubing is done:

.1	Clean the deposits from the system as specified in 2.1.2 and 3.4.

.2	Chemically treat the system with a corrosion and scale inhibitor and biocide specified in 2.2 and 3.5.

END OF DATA SHEETS

1.	General

1.1	INTENT

.1	This Section specifies services and material required for onsite, cleaning and chemical treatment of a multi-metal, condenser water system.

1.2	RELATED Requirements

.1	Mechanical Spare Parts and Maintenance Materials:	Section 20 00 23.

.2	Chemical Cleaning and Treatment Equipment:	Section 23 25 01.

.3	Chemical Cleaning and Treatment - General Requirements:	Section 23 25 02.

1.3	REFERENCE DOCUMENTS

.1	American Society for Testing and Materials (ASTM):

| .1 | ASTM D2688-05 | Standard Test Methods for Corrosivity of Water in the Absence of Heat Transfer (Weight Loss Methods) |
| --- | --- | --- |

.2	Alberta Infrastructure Documents:

| .1 | Alberta Infrastructure Water Treatment Program Manual (available on the Alberta Infrastructure Website) |
| --- | --- |

1.4	PERFORMANCE REQUIREMENTS

.1	Clean condenser water system to remove oil, grease, silt, and rust and leave metal surfaces well passivated.

.2	Chemically treat and maintain condenser water system to meet following standards:

| Parameter | Control Limits |
| --- | --- |
| Suspended solids: | Nil |
| Iron Corrosion Rate: | stable rate, 2.0 mils per year maximum. |
| Copper Corrosion rate: | stable rate, 0.2 mils per year maximum. |
| Total Plate Count: | 103 organisms/mL maximum. |
| pH: | 8.0-9.5. |
| Total Dissolved Solids: | 1200 S/cm (micro siemens/cm) maximum. |
| Total Hardness: | 650 mg/L CaCO3 maximum. |
| Total Alkalinity: | 350 mg/L CaCO3 maximum. |
| Phosphonate or Poly phosphate: | Manufacturer’s recommended written control limits. |

1.5	SUBMITTALS

.1	In addition to submittal requirements specified in Section 23 25 02, submit following information:

.1	Written report of actual cleaning activities including:

.1	Times.

.2	System status.

.3	Problems encountered.

.4	Actions taken.

.5	Composition of cleaning & spent cleaning solutions.

.6	Inspection results.

.7	Water test records for:

.1	pH level.

.2	Total dissolved solids concentration.

.3	Total hardness concentration.

.4	Total alkalinity concentration.

.5	Total place count bacteria concentration.

.6	Corrosion coupon weights and corrosion rates.

.7	Phosphonate or poly phosphate concentration.

.2	Statement which confirms that with chemical treatment used, quality of system effluent will be in compliance with local municipal sewer bylaws.

2.	Products

2.1	CLEANING CHEMICALS

SPEC NOTE:  Cleaning solution is not required for evaporative condenser water systems.

.1	Cleaning Solution:  neutral pH cleaning solution which is capable of removing oil, grease, and rust from metal surfaces of system and passivating cleaned metal surfaces of system.  Cleaning solution shall include:

.1	Low foaming non-ionic surfactant for penetrating oily and greasy deposit surfaces.

.2	Solvent for dissolving oil and grease.

.3	Dispersant for dissolving rust.

.4	Reducing agent for corrosion control.

.5	Ferrous and non-ferrous metal corrosion inhibitors.

SPEC NOTE:  Specify deposit removal cleaning solution for existing systems only.

.2	Deposit Removal Cleaning Solution: blended neutral pH cleaning solution which is capable of removing scale and iron deposits, destroying bacteria, and passivating metal surfaces of system.

2.2	CHEMICAL TREATMENT CHEMICALS

.1	Scale and Corrosion Inhibitor: containing following components, as a minimum requirement:

.1	Phosphonate or poly phosphate based.

.2	Dispersant.

.3	Ferrous and non-ferrous corrosion inhibitor.

.2	Biocide: compatible with scale and corrosion inhibitor.

2.3	CORROSION COUPONS

.1	Corrosion Coupons shall be supplied and installed by the Minister after the system has been cleaned, is fully operational and treated.

2.4	WATER TEST EQUIPMENT

.1	Supply one of each of the following water test kits specified in Section 23 25 02:

.1	pH test kit.

.2	Alkalinity test kit.

.3	Total Hardness test kit.

.4	TDS or Conductivity Meter.

.5	Dipslides for total plate count bacteria measurement.

.6	Corrosion inhibitor test kit.

.7	Phosphonate or poly phosphate test kit.

3.	Execution

3.1	EQUIPMENT INSTALLATION

.1	Prior to performing chemical treatment work ensure following work specified in Section 23 25 01 has been completed:

.1	Chemical metering system.

.2	Total dissolved solids control system.

.3	Corrosion coupon rack as per detail drawing 23 25 01.

3.2	CLEANING - GENERAL

SPEC NOTE:  Cleaning is not required for evaporative condenser water systems.

.1	By-pass the cooling tower using carbon steel blinds and clean/inert temporary piping prior to the cleaning process.

.2	Maintain following conditions during cleaning process:

.1	Manual and automatic valves are in full open position.

.2	By-pass valves are operated to ensure full flow through entire system.

.3	Safety devices, including pressure relief valves, flow switches, and pressure switches are functioning.

.4	System is operated with a minimum pressure of 35 kPa(g) at highest point.

.5	System pumps may be used to circulate cleaning solution.

.6	Fine mesh strainers for system pump and control valve strainer baskets are installed and cleaned as required.

3.3	CLEANING PROCEDURE

.1	Step 1:  Fill system with domestic water, establish circulation, and heat system contents to a temperature of 60°C.

.2	Step 2:  After two hours of circulation, collect water samples from at least three different locations in system.  If these samples contain suspended solids, clean out strainer baskets, drain system, and repeat steps 1 & 2.

.3	Step 3:  Blend in prepared concentration cleaning solution, established circulation, and maintain system temperature at 60°C for at least three days.

.4	Step 4:  Dump spent cleaning solution to disposal, fill system with domestic water, circulate system contents for at least two hours, dump spent rinse water to disposal.

.5	Step 5:  Fill system with domestic water and repeat step 4 until water samples collected from system are free of oil, grease, and suspended solids.

.6	Step 6:  Drain system completely, including all system low points and perform visual inspections of metal surfaces at three different locations.

.7	Complete steps 4, 5 & 6 within a 24 hour period.

.8	If metal surfaces contain oil, grease or silt, fill system with domestic water and repeat steps 3, 4, 5 & 6.

.9	Immediately after inspection is completed, install operating pump and control valve strainers, fill system with domestic water, blend in chemical treatment solution until its concentration in system is at an acceptable level, pass system water through corrosion coupon rack.

SPEC NOTE:  Specify deposit removal procedure for cleaning of existing systems.

3.4	DEPOSIT REMOVAL PROCEDURE

.1	Step 1:  Fill system with domestic water, establish circulation, and heat system contents to a temperature of 60°C;

.2	Step 2:  Blend in prepared concentrated cleaning solution for removal of deposits etc., establish circulation, and maintain system temperature at 60°C until total iron concentration stabilizes;

.3	Step 3:  Dump spent cleaning solution to disposal, fill system with domestic water, circulate system contents for at least two hours, and drain spent rinse water from various locations in system to disposal;

.4	Step 4:  Fill system with domestic water and repeat step 3 until water samples collected from system are free of suspended material;

.5	Step 5:  Drain system and perform visual inspections of metal surfaces at three different locations;

.6	Complete steps 3, 4, & 5 within a 24 hour period.

.7	Step 6:  If metal surfaces contain scale or iron deposits and are not passivated, fill system with domestic water and repeat steps 2, 3, 4 & 5.

3.5	OPERATION MAINTENANCE UNTIL INTERIM ACCEPTANCE

.1	Perform following minimum routine maintenance until Interim Acceptance of the Work:

.1	Maintain control limits specified under “Performance Requirements”.  Add chemicals as required.

.2	Test water samples of system 2 to 3 times per week for the following:

.1	pH levels.

.2	Total dissolved solids.

.3	Total hardness.

.4	Total alkalinity levels.

.5	Phosphonate or poly phosphate concentration.

.4	Test water samples of system once per month for total plate count bacteria concentration.

.2	Document water analyses results, quantities and dates chemicals added on chemical treatment report form.

3.6	Waste Water Disposal

.1	Wastewater discharged into a municipal sanitary sewer system from existing or new systems shall be within the limits established by local authorities.  Where no local limits have been established, stay within limits specified in “Alberta Infrastructure Water Treatment Program Manual, Section I - Environmental Guideline”.

3.7	CHEMICAL CLEANING AND TREATMENT SCHEDULE FOR RENOVATED SYSTEMS

SPEC NOTE:  Schedule cleaning requirements for renovated condenser water systems based on the guidelines on Page 01.

.1	Clean and treat renovated condenser systems as follows:

.1	New piping - isolated from rest of system:

.1	Chemically clean piping.

.2	Chemically treat entire system with corrosion inhibitor.

.2	[                                            ]:

.1	[                                            ].

.2	[                                            ].

.3	[                                            ].

END OF SECTION