Section Cover Page

Section 23 34 00 2010-12-31 Fans

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Related Requirements

1.2	Product Options and Substitutions

1.3	Submittals

1.4	Quality Assurance

1.5	Delivery, Storage, and Handling

2.	Products

2.1	General

2.2	Centrifugal Fans

2.3	Roof Mounted Fans

2.4	Belted Vent Sets

2.5	Axial Fans

2.6	Propeller Fan

2.7	Bathroom Exhaust Fans

2.8	Kitchen Range Hoods

3.	Execution

3.1	Performance

3.2	Installation

3.3	Priming

3.4	Starting and Testing

3.5	Fan Schedule

1.	General

1.1	RELATED Requirements

.1	General Mechanical Starting and Testing Requirements:	Section 23 08 13.

.2	Mechanical Equipment Starting and Testing:	Section 23 08 23.

1.2	PRODUCT OPTIONS AND SUBSTITUTIONS

.1	Refer to Division 01.

.2	Substitute products shall not decrease motor wattage, increase noise level, increase tip speed by more than 10%, or increase inlet air velocity by more than 20%, from that specified.

1.3	SUBMITTALS

.1	Shop Drawings:

.1	Submit shop drawings in accordance with Section 20 00 13 – Mechanical General Requirements.

.2	Submit with shop drawings acoustical data and fan curves showing fan performance with fan and system operating point plotted on curves.

1.4	QUALITY ASSURANCE

SPEC NOTE:  Alberta Infrastructure policy is to require AMCA rated equipment for relatively large equipment and installations.  Use discretion in requiring AMCA rating seal.

.1	Conform to AMCA Bulletins regarding construction and testing.  Fans shall bear AMCA certified rating seal.

1.5	Delivery, Storage, and Handling

.1	Separate waste materials for [reuse] [and] [recycling] in accordance with Section 01 74 19 – Waste Management and Disposal.

2.	Products

2.1	GENERAL

.1	Statically and dynamically balance fans so no objectionable vibration or noise is transmitted to occupied areas of the building.

.2	Provide balanced variable sheaves for motors 10 kW and under and fixed sheave to 15 kW and over.

.3	Fans shall be capable of accommodating static pressure variations of +10% with no objectionable operating characteristics.

2.2	CENTRIFUGAL FANS

.1	Fabricate with multi-blade wheels in heavy gauge steel housing reinforced for service encountered.

.2	Provide V-belt drives with fan and motor mounted on reinforced, rigid steel base with adjustable motor mount.

.3	Provide heavy duty, self-aligning, anti-friction bearings with external lubrication.

.4	Provide where indicated variable inlet vanes.

.5	Provide access door and drain connection to  scroll.

.6	Except for packaged air units, belted vent sets and as otherwise noted, centrifugal fans over 430 mm diameter shall have die formed air foil blades welded to side and back plate.

2.3	ROOF MOUNTED FANS

.1	Provide V-belt drives with fan and motor mounted to main housing through neoprene anti-vibration pads.

.2	Heavy aluminum dome type housings shall be reinforced as necessary on sizes with 500 mm wheel and larger.

.3	Provide with multi-blade, rattle free, backdraft damper with felt lined blade edges, birdscreen, disconnect switch and curb caps.

2.4	BELTED VENT SETS

.1	Comply generally with requirements of centrifugal fans suitable for pressures to 1 kPa

.2	Provide with multi-blade rattle free backdraft damper with felt lined blades edges.

2.5	AXIAL FANS

.1	Provide either adjustable die cast impeller blades with motor integral part of hub design or die formed blades with belt drive and motor mounted outside air stream.

.2	Extend lubrication fittings to outside of fan casing.  Terminal box shall be external.

.3	Housing shall have flanges for connection of ductwork.  When not connected to ducting, provide inlet cones.

.4	Provide easy access to fan wheel for varying blade angle setting during air balancing.

.5	Provide variable inlet vanes where indicated.

.6	Fans operating at over 370 Pa shall be of vane-axial design for improved operating efficiency.

2.6	PROPELLER FAN

.1	Directly connect steel or aluminum blade fans with heavy hubs to motor.

.2	Motor shall have self-aligning ball or sleeve bearings with adequate lubricating arrangements.

.3	Mountings shall be cast or die formed to smooth curves.  Supply size to fit openings provided.

.4	Provide safety screens in inlet and backdraft dampers on outlet.

.5	Use neoprene vibration isolation between fan assembly and mounting plate.

2.7	BATHROOM EXHAUST FANS

.1	Provide multi-blade, forward curved wheel in steel housing for between stud mounting.

.2	Resiliently mount direct driven fan and motor.  Motor shall be plug-in type with permanently lubricated bearings.

.3	Provide one piece aluminum intake grille.

2.8	KITCHEN RANGE HOODS

.1	Resiliently mount multi-blade direct driven fan and motor.  Motor shall be two-speed plug-in type with permanently lubricated bearings.

.2	Finish hood in [white] [     ] baked on enamel, with rocker type switches for light and two-speed fan.  Provide washable type filter of aluminum mesh.  [Provide matching colour back splash].

3.	Execution

3.1	PERFORMANCE

.1	Fan performance based on [sea level] [     ] conditions.

.2	Refer to Fan Schedule.

3.2	INSTALLATION

.1	Where inlet or outlet is exposed, provide safety screen.

.2	Provide belt guards on belt driven fans.

.3	Supply and install sheaves as necessary for final air balancing.

.4	Set roof mounted fans on curbs 200 mm minimum above roof.  Provide acoustic insulation on duct to below roof line and on fan inlet plenum, and drip pan for collecting condensation.

3.3	PRIMING

.1	Prime coat fan wheels and housing factory inside and outside.  Prime coating on aluminum parts is not required.

.2	Provide two additional coats of paint on fans handling air downstream of humidifiers.

3.4	STARTING AND TESTING

.1	Start and test fans as specified in Section 23 08 13 and 23 08 23.

3.5	FAN SCHEDULE

| Fan No. | F-1 | F-2 | F-3 | F-4 |
| --- | --- | --- | --- | --- |
| Manufacturer |  |  |  |  |
| Model |  |  |  |  |
| Type |  |  |  |  |
| Class |  |  |  |  |
| Arrangement |  |  |  |  |
| Capacity L/s |  |  |  |  |
| S.P. kPa |  |  |  |  |
| Motor kW |  |  |  |  |
| Accessories |  |  |  |  |

END OF SECTION