Section Cover Page

Section 23 52 23 2010-12-31 Cast Iron Boilers

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if project: .1 is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Related Requirements

1.2	Reference Documents

1.3	Submittals

1.4	Quality Assurance

1.5	Delivery, Storage, and Handling

1.6	LEED Requirements

2.	Products

2.1	Type

2.2	Construction

2.3	Steam Boiler Trim

2.4	Hot Water Boiler Trim

2.5	Fuel Burning System

3.	Execution

3.1	Performance

3.2	Starting and Testing

LEED Notes:

Refer to Section 01 35 18 – LEED Requirements for:

.1	Requirements necessary for this project to obtain points required for certification.

.2	Confirmation of LEED prerequisites and credits affecting this Section; not all are mandatory for certification

Maintain built-in sustainability regardless of LEED requirements for:

.1	Recycling, reuse of materials, components and assemblies.

.2	Diversion of construction waste from landfills.

.3	Use of recycled materials, local materials, rapidly renewable and durable materials.

.4	Maintain healthy indoor environment during constructing.

.5	Provide for thermal comfort, access to views and daylight for indoor spaces.

.6	Foster innovation into facility design and planning.

LEED Credits:

Energy & Atmosphere

Prerequisite 2 – Minimum Energy Performance

Note:  Though prerequisites do not contribute to a projects point score, they are mandatory and MUST be met for a project to receive LEED Canada – NC certification.

Credit 1 – Optimize Energy Performance

Materials & Resources

Credit 2 – Construction Waste Management

1.	General

1.1	RELATED Requirements

.1	General Mechanical Starting and Testing Requirements:	Section 23 08 13.

.2	Mechanical Equipment Starting and Testing:	Section 23 08 23.

1.2	REFERENCE DOCUMENTS

.1	Canada Green Building Council (CaGBC):

| .1 | LEED Canada 2009 Rating System | LEED Canada for New Construction and Major Renovations. LEED Canada for Core and Shell Development. Website: www.cagbc.org |
| --- | --- | --- |

SPEC NOTE: Specify the above only if this is a LEED project

.2	National Research Council of Canada (NRC):

| .1 | MNECB 1997, Model National Energy Code for Buildings |
| --- | --- |

1.3	submittals

.1	Product Data:

.1	Submit manufacturer’s product data in accordance with Section 20 00 13 – Mechanical General Requirements

.1	Submit copies of manufacturer’s product literature, specifications and datasheets.

.2	Shop Drawings:

.1	Submit shop drawings in accordance with Section 20 00 13 – Mechanical General Requirements.

.1	Indicate the following information:

.1	General arrangement showing terminal points, instrumentation test connections.

.2	Clearances for operation, maintenance, servicing, tube cleaning, tube replacement.

.3	Foundations with loadings, anchor bolt arrangements.

.4	Piping hook-ups.

.5	Equipment electrical drawings.

.6	Burners and controls.

.7	All miscellaneous equipment.

.8	Flame safety control system.

.9	Breeching and stack configuration.

.10	[Stack emission continuous monitoring system to measure C0, 0, N0x, S0, stack temperature and smoke density of flue gases].

.2	Indicate the following engineering information:

.1	Boiler efficiency at 25%, 50%, 75%, 100%, [and 110% ] of design capacity.

.2	Radiant heat loss at 100% design capacity.

.3	Closeout Submittals:

.1	Submit operations and maintenance data for incorporation into manuals specified in Section 20 01 06 – Mechanical Operation and Maintenance Manual.

1.4	QUALITY ASSURANCE

.1	Comply with Provincial Regulations and have CSA approval.

.2	Units shall be approved and labelled by Underwriter's Laboratories.

1.5	Delivery, Storage, and Handling

.1	Separate waste materials for [reuse] [and] [recycling] in accordance with Section 01 74 19 – Waste Management and Disposal.

1.6	leed requirements

.1	EA Prerequisite 2 – Minimum Energy Performance

.2	EA Credit 1 – Optimize Energy Performance

.1	Objectives: reduce the design energy consumption relative to the energy consumption of a reference building designed to MNECB standards.

.2	Requirements: submit information indicating efficiency values for installed boilers.

2.	Products

2.1	TYPE

.1	Provide [hot water] [steam] boiler suitable for [forced] [induced] [natural] draft with insulated jacket, sectional cast iron heat exchanger, [gas] [oil] [gas-oil] burning system, refractory, controls and boiler trim.

.2	For forced draft firing, provide water design consisting of water backed combustion area with water circulating all around firebox.  Refractory chamber or separate base not required.

2.2	CONSTRUCTION

.1	Assemble of cast iron sections conforming to ASME Code requirements and tests for maximum working pressure of 100 kPa - 200 kPa water.

.2	Permanently seal sections using asbestos rope seal and short draw rods for each pair of sections.

.3	Flue passages shall be readily accessible without use of special tools.  Provide adequate clean-out and access doors, and openings including observation ports and relief openings.

.4	Provide structural steel base with front plate, removable panels and lifting lugs.

.5	Insulate entire boiler with glass fiber and finish with steel cover jacket with factory applied baked enamel.

2.3	STEAM BOILER TRIM

.1	Provide pressure gauge and ASME rated pressure relief valve.

.2	Provide water column with cocks, gauge glass set and blowdown valves for glass and column.

.3	Provide low water cut-off with manual reset integral with water column to automatically prevent burner operation when boiler water falls below safe level.

.4	Provide boiler condensate return pump control integral with water column to automatically maintain water level by controlling pump operation.

.5	Operating pressure controller shall control burner to maintain steam pressure setting.

.6	Limit pressure controller shall control burner to prevent steam pressure from exceeding safe system pressure.

2.4	HOT WATER BOILER TRIM

.1	Provide combination water pressure and temperature gauge, and ASME rated pressure relief valves.

.2	Provide low water cut-off with manual reset to automatically prevent burner operation when boiler water falls below safe level.

.3	Operating temperature controller [with outdoor reset] shall control burner operation to maintain boiler water temperature.  [Controller shall be electronic].

.4	Limit temperature controller shall control burner to prevent boiler water temperature from exceeding safe system temperature.

.5	Provide boiler air vent tapping.

2.5	FUEL BURNING SYSTEM

.1	General:  Burner operation shall be [on-off] [hi-low] [modulating] [with low fire position for ignition].

.2	Oil Burner:  [High] [Low] pressure atomizing type with electric  ignition.

.3	Gas Burner:  Atmospheric or power type with electric ignition and gas pressure regulator.

.4	Combination Gas-Oil Burner: Burner for gas and burners for oil, built as single unit, without need of interchanging gas burner and oil burner with gas pressure regulator.  Include oil-gas selector switch for changeover.

.5	Collector and Draft Hood:  Provide atmospheric gas-fired boiler with natural draft operation equipment as regularly supplied by boiler manufacturer.

.6	Controls:  Pre-wired, factory assembled electronic controls in control cabinet with flame scanner or detector, programming control, relays and switches.  Provide pre-purge and post-purge ignition and shut-down of burner in event of ignition pilot and main flame failure with manual reset.

3.	Execution

3.1	PERFORMANCE

.1	Provide [     ] boilers for producing [steam] [hot water] each with gross input [     ]W gross output [     ]W at sea level.

.2	Unit[s] shall be [     ] Model [     ].

3.2	STARTING AND TESTING

.1	Start and test boilers as specified in Section 23 08 13 and 23 08 23.

END OF SECTION