Section Cover Page

Section 23 52 33 2010-12-31 Water Tube Boilers

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if project: .1 is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Related Requirements

1.2	Reference Documents

1.3	Submittals

1.4	Quality Assurance

1.5	Delivery, Storage, and Handling

1.6	LEED Requirements

2.	Products

2.1	Type

2.2	Construction

2.3	Trim

2.4	Fuel Burning System

2.5	Controls

3.	Execution

3.1	Performance

3.2	Starting and Testing

LEED Notes:

Refer to Section 01 35 18 – LEED Requirements for:

.1	Requirements necessary for this project to obtain points required for certification.

.2	Confirmation of LEED prerequisites and credits affecting this Section; not all are mandatory for certification

Maintain built-in sustainability regardless of LEED requirements for:

.1	Recycling, reuse of materials, components and assemblies.

.2	Diversion of construction waste from landfills.

.3	Use of recycled materials, local materials, rapidly renewable and durable materials.

.4	Maintain healthy indoor environment during constructing.

.5	Provide for thermal comfort, access to views and daylight for indoor spaces.

.6	Foster innovation into facility design and planning.

LEED Credits:

Energy & Atmosphere

Prerequisite 2 – Minimum Energy Performance

Note:  Though prerequisites do not contribute to a projects point score, they are mandatory and MUST be met for a project to receive LEED Canada – NC certification.

Credit 1 – Optimize Energy Performance

Materials & Resources

Credit 2 – Construction Waste Management

1.	General

1.1	RELATED Requirements

.1	General Mechanical Starting and Testing Requirements:	Section 23 08 13.

.2	Mechanical Equipment Starting and Testing:	Section 23 08 23.

1.2	REFERENCE DOCUMENTS

.1	Canada Green Building Council (CaGBC):

| .1 | LEED Canada 2009 Rating System | LEED Canada for New Construction and Major Renovations. LEED Canada for Core and Shell Development. Website: www.cagbc.org |
| --- | --- | --- |

SPEC NOTE: Specify the above only if this is a LEED project

.2	National Research Council of Canada (NRC):

| .1 | MNECB 1997, Model National Energy Code for Buildings |
| --- | --- |

1.3	submittals

.1	Product Data:

.1	Submit manufacturer’s product data in accordance with Section 20 00 13 – Mechanical General Requirements

.1	Submit copies of manufacturer’s product literature, specifications and datasheets.

.2	Shop Drawings:

.1	Submit shop drawings in accordance with Section 20 00 13 – Mechanical General Requirements.

.1	Indicate the following information:

.1	General arrangement showing terminal points, instrumentation test connections.

.2	Clearances for operation, maintenance, servicing, tube cleaning, tube replacement.

.3	Foundations with loadings, anchor bolt arrangements.

.4	Piping hook-ups.

.5	Equipment electrical drawings.

.6	Burners and controls.

.7	All miscellaneous equipment.

.8	Flame safety control system.

.9	Breeching and stack configuration.

.10	[Stack emission continuous monitoring system to measure C0, 0, N0x, S0, stack temperature and smoke density of flue gases].

.2	Indicate the following engineering information:

.1	Boiler efficiency at 25%, 50%, 75%, 100%, [and 110% ] of design capacity.

.2	Radiant heat loss at 100% design capacity.

.3	Closeout Submittals:

.1	Submit operations and maintenance data for incorporation into manuals specified in Section 20 01 06 – Mechanical Operation and Maintenance Manual.

1.4	QUALITY ASSURANCE

.1	Comply with Provincial Regulations and have CSA approval.

.2	Units shall be approved and labelled by Underwriter's Laboratories.

1.5	Delivery, Storage, and Handling

.1	Separate waste materials for [reuse] [and] [recycling] in accordance with Section 01 74 19 – Waste Management and Disposal.

SPEC NOTE: Delete the following if project is not pursuing LEED certification or if the following credit is not being pursued.

1.6	leed requirements

.1	EA Prerequisite 2 – Minimum Energy Performance

.2	EA Credit 1 – Optimize Energy Performance

.1	Objectives: reduce the design energy consumption relative to the energy consumption of a reference building designed to MNECB standards.

.2	Requirements: submit information indicating efficiency values for installed boilers.

2.	Products

2.1	TYPE

.1	Provide hot water, natural draft boiler with horizontal grid fin tube heat exchanger, gas burning system refractory combustion chamber, controls and boiler trim.

2.2	CONSTRUCTION

.1	Assemble of finned copper tube heat exchanger within combustion chamber conforming to ASME Code requirements and tested for maximum working pressure of 1100 kPa.

.2	Line combustion chamber with interlocking refractory insulating panels of vermiculite, high temperature cement, asbestos fiber and refractory clay.

.3	Fabricate exchanger with finned copper tubing with baffles and sealed into bronze or cast iron headers with silicon O-ring gaskets.

.4	Finish with galvanized steel jacket with factory applied baked enamel.

.5	Heat exchanger shall be cleanable from left or right side.  Cleaning from one side without removal of external piping.

2.3	TRIM

.1	Provide ASME rated pressure relief valve set at 310 kPa - 410 kPa.

.2	Provide low water cut-off with manual reset and inlet flow switch to automatically prevent burner operation when water falls below safe level or there is no flow through boiler.

.3	Provide operating temperature controller [with outdoor reset] to control burner operation to maintain supply water temperature.  [Controller shall be electronic].

.4	Limit temperature controller with automatic reset shall control burner to prevent boiler water temperature from exceeding safe system temperature.

2.4	FUEL BURNING SYSTEM

.1	Atmospheric gas type burner shall be [on-off] [hi-low] [modulating] firing with [gas electric] [standing pilot] ignition and gas pressure regulator.

.2	Provide fuel gas collector and draft hood.

2.5	CONTROLS

.1	Provide pre-wired, factory assembled electric controls enclosed in cabinet.  Control string includes pilot safety and thermocouple transformer, 24V gas valve, manual main and pilot valves, and junction box.

3.	Execution

3.1	PERFORMANCE

.1	Provide [     ] boilers each with gross input [     ]W gross output [     ]W, at sea level.

.2	Unit[s] shall be [     ] Model [     ].

3.2	STARTING AND TESTING

.1	Start and test boilers as specified in Section 23 08 13 and 23 08 23.

END OF SECTION