Section Cover Page

Section 23 61 16 Reciprocating Refrigeration 2010-12-31 Compressor

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if project: .1 is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Quality Assurance

1.2	Submittals

2.	Products

2.1	Type

2.2	Compressor Construction

2.3	Controls

3.	Execution

3.1	Installation

3.2	Performance

LEED Notes:

Refer to Section 01 35 18 – LEED Requirements for:

1.	Requirements necessary for this project to obtain points required for certification.

2.	Confirmation of LEED prerequisites and credits affecting this Section; not all are mandatory for certification

Maintain built-in sustainability regardless of LEED requirements for:

.1	Recycling, reuse of materials, components and assemblies.

.2	Diversion of construction waste from landfills.

.3	Use of recycled materials, local materials, rapidly renewable and durable materials.

.4	Maintain healthy indoor environment during constructing.

.5	Provide for thermal comfort, access to views and daylight for indoor spaces.

.6	Foster innovation into facility design and planning.

LEED Credits:

Energy & Atmosphere

Prerequisite 2 – Minimum Energy Performance

Prerequisite 3 – Fundamental Refrigerant Management

Note:  Though prerequisites do not contribute to a projects point score, they are mandatory and MUST be met for a project to receive LEED Canada – NC certification.

Credit 1 – Optimize Energy Performance

Credit 4 – Enhanced Refrigerant Management

Note:  Chlorofluorocarbons (CFCs) are a class of chemicals used in refrigeration equipment that contribute to the destruction of the ozone layer.  Hydrochlorofluorocarbons (HCFCs) based refrigerants are more environmentally friendly than CFC based refrigerants but still have a high ozone depletion potential (OPD).  Energy and Atmosphere prerequisite 3 requires that LEED projects eliminate CFCs in all base building HVAC&R systems. Energy and Atmosphere credit 4 awards points for using HVAC and refrigeration equipment that is free of HCFCs.

1.	General

1.1	QUALITY ASSURANCE

.1	Conform to requirements of CSA, UL Provincial and Municipal Codes.

.2	Units shall be product of manufacturer regularly engaged in production of refrigeration units and who issues complete catalogue data on such products.

1.2	SUBMITTALS

.1	Product Data:

.1	Submit manufacturer’s product data in accordance with Section 20 00 13 – Mechanical General Requirements.

.2	Shop Drawings:

.1	Submit shop drawings in accordance with Section 20 00 13 – Mechanical General Requirements.

.1	With compressor shop drawings, submit schematic layouts incorporating condenser, coils, piping and accessories for complete system.  Include pipe sizing data.

2.	Products

2.1	TYPE

.1	Provide compressor unit consisting of accessible hermetic motor-compressor with cylinder unloaders, crankcase heater, suction and discharge service valves, spring isolators and remote mounted control panel.

2.2	COMPRESSOR CONSTRUCTION

.1	Construct compressor unit with cast iron housing and head, heat treated forged steel or ductile iron shaft, aluminum alloy connecting rods, automotive type pistons with rings to prevent leakage, high strength alloy suction and discharge valves and oil immersed sealing surfaces.  Statically and dynamically balance rotating parts.

.2	Provide reversible oil pump lubrication system to ensure adequate lubrication during starting, stopping and normal operation.

.3	Provide compressor with automatic capacity reduction equipment consisting of suction valve unloaders.  Lifting mechanism shall be operated by [oil pressure] [gas discharge pressure] [solenoid valve].  Provide for unloaded compressor start.

.4	Compressor motor shall be constant speed [     r/min] suction gas cooled with overheating protection designed for [full] [reduced] voltage starting complete with starter.

.5	Provide crankcase heater to evaporate refrigerant returning to crankcase during shut down.  Energize heater [continuously] [when compressor is not operating].

2.3	CONTROLS

.1	Provide the compressor with adjustable high and low pressure cutouts and an automatic differential oil pressure safety control.

.2	Factory wired steel control panel shall contain automatic and manual capacity controllers, switches for manual or automatic operation of oil pump, switch and pilot light for crankcase heater, terminal strip for connection to interface equipment, and gauges to show high pressure, low pressure and oil pressure.

3.	Execution

3.1	INSTALLATION

.1	Install compressor on concrete foundation with sole plates and rubber in shear isolators.  Level, grout and bolt in place.

.2	Arrange piping for easy dismantling.

3.2	PERFORMANCE

.1	Provide [     ] semi-hermetic reciprocating compressor[s], [each] having a capacity of [     ]kW of refrigeration at an operating suction temperature of [     ]°C condensing temperature of [     ]°C and [      ]kW input.

.2	Unit[s] shall be [       ] Model [      ].

END OF SECTION