Section Cover Page

Section 23 63 14 2010-12-31 Air Cooled Refrigerant Condensers

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if project: .1 is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Related Requirements

1.2	Submittals

1.3	Quality Assurance

2.	Products

2.1	Type

2.2	Cabinet

2.3	Condenser Coils

2.4	Fans and Motors

2.5	Controls

3.	Execution

3.1	Performance

3.2	System Charging

3.3	Seasonal Start-up and Shut-down

3.4	Starting and Testing

LEED Notes:

Refer to Section 01 35 18 – LEED Requirements for:

1.	Requirements necessary for this project to obtain points required for certification.

2.	Confirmation of LEED prerequisites and credits affecting this Section; not all are mandatory for certification

Maintain built-in sustainability regardless of LEED requirements for:

.1	Recycling, reuse of materials, components and assemblies.

.2	Diversion of construction waste from landfills.

.3	Use of recycled materials, local materials, rapidly renewable and durable materials.

.4	Maintain healthy indoor environment during constructing.

.5	Provide for thermal comfort, access to views and daylight for indoor spaces.

.6	Foster innovation into facility design and planning.

LEED Credits:

Energy & Atmosphere

Prerequisite 2 – Minimum Energy Performance

Prerequisite 3 – Fundamental Refrigerant Management

Note:  Though prerequisites do not contribute to a projects point score, they are mandatory and MUST be met for a project to receive LEED Canada – NC certification.

Credit 1 – Optimize Energy Performance

Credit 4 – Enhanced Refrigerant Management

Note:  Chlorofluorocarbons (CFCs) are a class of chemicals used in refrigeration equipment that contribute to the destruction of the ozone layer.  Hydrochlorofluorocarbons (HCFCs) based refrigerants are more environmentally friendly than CFC based refrigerants but still have a high ozone depletion potential (OPD).  Energy and Atmosphere prerequisite 3 requires that LEED projects eliminate CFCs in all base building HVAC&R systems. Energy and Atmosphere credit 4 awards points for using HVAC and refrigeration equipment that is free of HCFCs.

1.	General

1.1	RELATED Requirements

.1	Mechanical Spare Parts and Maintenance Materials:	Section 20 00 23.

.2	General Mechanical Starting and Testing Requirements:	Section 23 08 13.

.3	Mechanical Equipment Starting and Testing:	Section 23 08 23.

1.2	SUBMITTALS

.1	Shop Drawings:

.1	Submit shop drawings in accordance with Section 20 00 13 – Mechanical General Requirements.

.1	Submit with shop drawings, schematic layouts showing condenser, refrigeration compressors, cooling coils, refrigerant piping and accessories required for complete system.

.2	Submit complete pipe sizing data.

1.3	QUALITY ASSURANCE

.1	Conform to requirements of CSA, UL, Provincial and Municipal Codes.

.2	Units shall be product of manufacturer regularly engaged in production of refrigeration units and who issues complete catalogue data on such products.

2.	Products

2.1	TYPE

.1	Provide packaged, factory assembled, prewired unit, suitable for [outdoor] [indoor] use consisting of casing, condensing coil and fans, integral sub-cooling coil, controls, liquid accumulator, [wind deflector], screens.

2.2	CABINET

.1	Construct of heavy gauge galvanized steel with baked enamel finish, easily removed access doors or panels with quick fasteners.

2.3	CONDENSER COILS

.1	Seamless copper tubing with mechanically bonded aluminum fins.

.2	Provide sub-cooling circuit with liquid accumulator[s].

2.4	FANS AND MOTORS

.1	Fans:  [Propeller], [Centrifugal], [draw-thru], [blow- thru], [direct drive], [belt drive], statically and dynamically balanced. Provide guards as required. Bearings shall be roller or ball type with grease fittings extended to outside of casing.

.2	Motors:  Permanently lubricated ball bearing motors with built-in current and overload protection.

2.5	CONTROLS

.1	Provide factory wired and mounted control panel containing fan motor contactors, [fan cycling thermostats], [head pressure damper controls], compressor interlock and control transformer.

.2	Provide controls to permit operation down to [     ]°C ambient temperature at minimum load.

3.	Execution

3.1	PERFORMANCE

.1	Provide [       ] air cooled refrigerant condensing unit[s], [each] having a heat rejection capacity of [     ]W with a saturated suction temperature of [     ]°C and air entering condenser at [     ]°C, condensing temperature [     ]°C, condenser air flow [    L/s], fan motor[s] [     ] at [     ]W.

.2	Unit[s] shall be [     ] Model [     ].\

3.2	SYSTEM CHARGING

.1	Provide initial charge of refrigerant and oil for each refrigeration system.  Replace all losses of oil and refrigerant until Interim Acceptance of the Work and losses due to equipment defects until Total Completion of the Work.

3.3	SEASONAL START-UP AND SHUT-DOWN

.1	For first year of operation provide cooling season start-up and winter season shut-down.

3.4	STARTING AND TESTING

.1	Start and test condensers as specified in Section 23 08 13 and 23 08 23.

END OF SECTION