Section Cover Page

Section 23 64 13 2010-12-31 Absorption Water Chillers

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if project: .1 is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

This Master Specification Section contains:

1.	This Cover Sheet

2.	Specification Section Text:

1.	General

1.1	Related Requirements

1.2	Shop Drawings

1.3	Quality Assurance

2.	Products

2.1	Pumps

2.2	Construction

2.3	Controls

2.4	Purge System

2.5	Automatic Decrystallization

2.6	Pressure Ratings

3.	Execution

3.1	Performance

3.2	Installation

3.3	Starting and Testing

LEED Notes:

Refer to Section 01 35 18 – LEED Requirements for:

1.	Requirements necessary for this project to obtain points required for certification.

2.	Confirmation of LEED prerequisites and credits affecting this Section; not all are mandatory for certification

Maintain built-in sustainability regardless of LEED requirements for:

.1	Recycling, reuse of materials, components and assemblies.

.2	Diversion of construction waste from landfills.

.3	Use of recycled materials, local materials, rapidly renewable and durable materials.

.4	Maintain healthy indoor environment during constructing.

.5	Provide for thermal comfort, access to views and daylight for indoor spaces.

.6	Foster innovation into facility design and planning.

LEED Credits:

Energy & Atmosphere

Prerequisite 2 – Minimum Energy Performance

Prerequisite 3 – Fundamental Refrigerant Management

Note:  Though prerequisites do not contribute to a projects point score, they are mandatory and MUST be met for a project to receive LEED Canada – NC certification.

Credit 1 – Optimize Energy Performance

Credit 4 – Enhanced Refrigerant Management

Note:  Chlorofluorocarbons (CFCs) are a class of chemicals used in refrigeration equipment that contribute to the destruction of the ozone layer.  Hydrochlorofluorocarbons (HCFCs) based refrigerants are more environmentally friendly than CFC based refrigerants but still have a high ozone depletion potential (OPD).  Energy and Atmosphere prerequisite 3 requires that LEED projects eliminate CFCs in all base building HVAC&R systems. Energy and Atmosphere credit 4 awards points for using HVAC and refrigeration equipment that is free of HCFCs.

1.	General

1.1	RELATED requirements

.1	General Mechanical Starting and Testing Requirements:	Section 23 08 13.

.2	Mechanical Equipment Starting and Testing:	Section 23 08 23.

1.2	SHOP DRAWINGS

.1	Product Data:

.1	Submit manufacturer’s product data in accordance with Section 20 00 13 – Mechanical General Requirements.

.2	Shop Drawings:

.1	Submit shop drawings in accordance with Section 20 00 13 – Mechanical General Requirements.

.1	Show on shop drawings equipment, piping and connections, valves, strainers thermostatic valves required for complete system.

.3	Closeout Submittals:

.1	Submit operations and maintenance data for incorporation into manuals specified in Section 20 01 06 – Mechanical Operation and Maintenance Manual.

1.3	QUALITY ASSURANCE

.1	Provide absorption water chiller[s], package type, factory assembled and product of manufacturer regularly engaged in production of unit of type and size specified, who issues complete catalogue data on such products.

.2	Manufacturer shall be responsible for selection and operation of components furnished by him. Provide written certification that components not furnished by him have been selected in accordance with his requirements.

2.	Products

2.1	PUMPS

.1	Solution and refrigerant pump[s] shall be self-contained hermetic centrifugal type, lubricated by lithium bromide solution of refrigerant.

.2	Pump motor shall be serviceable without breaking machine vacuum.

2.2	CONSTRUCTION

.1	Arrange components in one or two shells of corrosion resistant material. Fabricate absorber and generator of cupro-nickel tubes and evaporator and condenser of copper tubes rolled or silver brazed to tube sheets.  Provide adequate number of support sheets.  Tubes shall be individually replaceable.

.2	Provide removable water boxes [heads] of cast iron or welded steel, arranged to permit access to tube bundles.

.3	Insulate evaporator of two shell machines.

2.3	CONTROLS

.1	On or near chiller, mount steel control panel or panels containing terminal block, control transformer, pump motor starter[s], pump overload protection, low temperature cut-out, run lights of unit, pump[s] and purge system safeties, chilled water temperature controller, necessary pneumatic electric switches, valves and gauges.  Completely pre-wire and pre-pipe panels.

.2	Provide normally closed pneumatic [steam] [hot water] control valve. Provide demand limiter on valve to slow rate at which valve opens to minimum 5 minutes cycles.

.3	Provide unit complete with solution throttling device to increase art load economy and assure operation to 10 percent specified full load capacity, at 13 °C entering condenser water temperature.

2.4	PURGE SYSTEM

.1	Provide purge system to automatically or manually purge unit of non-condensibles, storing them external to unit so they cannot diffuse back into unit.

2.5	AUTOMATIC DECRYSTALLIZATION

.1	Provide for automatic decrystallization using lithium bromide solution.  Process shall be such to prevent crystallization while machine is running at shut-down.

2.6	PRESSURE RATINGS

.1	Design water spaces of absorber, condenser and evaporator for 1030 kPa minimum working pressure and test not less than 1.5 times maximum working pressure.

.2	Design steam space of concentrator for 350 kPa minimum working pressure and test not less than 1.5 times maximum working pressure.

.3	Design hot water space of concentrator for 1720 kPa minimum working pressure and test not less than 1.5 times maximum working pressure.

3.	Execution

3.1	PERFORMANCE

.1	Provide [     ] absorption water chillers[s], [each] having capacity of [     ]kW minimum of refrigeration when delivery [     ]L/s of chilled water at [     ]°C, when supplied with [     ]L/s of condensing water at [     ]°C and [     ]L/s of hot water, [     ]kg/hr of dry saturated steam  at [     ]°C fouling factor of not less than 0.0005 for evaporator and absorber-condenser. Water head loss through evaporator shall not exceed [     ]kPa.  Water head loss through absorber-condenser shall not exceed [     ]kPa. Water head loss through concentrator shall not exceed [     ]kPa.

.2	Unit shall be [      ] Model [      ].

3.2	INSTALLATION

.1	Adjust chiller in alignment on concrete foundations, sole plates, sub-bases and isolation. Level, grout and bolt in place.

.2	Arrange piping for easy dismantling to permit tube cleaning.

.3	Furnish and install necessary auxiliary water piping for oil cooling units and pure condensers.

.4	Provide initial charge of lithium bromide.

3.3	STARTING AND TESTING

.1	Start and test chillers as specified in Section 23 08 13 and 23 08 23.

END OF SECTION