Section Cover Page

Section 23 74 50 2010-12-31 Air Cooled Packaged Chillers

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if project: .1 is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Related Requirements

1.2	Submittals

1.3	Quality Assurance

2.	Products

2.1	Compressor

2.2	Evaporator

2.3	Condenser

2.4	Enclosures

2.5	Controls

3.	Execution

3.1	Performance

3.2	Installation

3.3	Starting and Testing

LEED Notes:

Refer to Section 01 35 18 – LEED Requirements for:

1.	Requirements necessary for this project to obtain points required for certification.

2.	Confirmation of LEED prerequisites and credits affecting this Section; not all are mandatory for certification

Maintain built-in sustainability regardless of LEED requirements for:

.1	Recycling, reuse of materials, components and assemblies.

.2	Diversion of construction waste from landfills.

.3	Use of recycled materials, local materials, rapidly renewable and durable materials.

.4	Maintain healthy indoor environment during constructing.

.5	Provide for thermal comfort, access to views and daylight for indoor spaces.

.6	Foster innovation into facility design and planning.

LEED Credits:

Energy & Atmosphere

Prerequisite 2 – Minimum Energy Performance

Prerequisite 3 – Fundamental Refrigerant Management

Note:  Though prerequisites do not contribute to a projects point score, they are mandatory and MUST be met for a project to receive LEED Canada – NC certification.

Credit 1 – Optimize Energy Performance

Credit 4 – Enhanced Refrigerant Management

Note:  Chlorofluorocarbons (CFCs) are a class of chemicals used in refrigeration equipment that contribute to the destruction of the ozone layer.  Hydrochlorofluorocarbons (HCFCs) based refrigerants are more environmentally friendly than CFC based refrigerants but still have a high ozone depletion potential (OPD).  Energy and Atmosphere prerequisite 3 requires that LEED projects eliminate CFCs in all base building HVAC&R systems. Energy and Atmosphere credit 4 awards points for using HVAC and refrigeration equipment that is free of HCFCs.

1.	General

1.1	RELATED requirements

.1	General Mechanical Starting and Testing Requirements:	Section 23 08 13.

.2	Mechanical Equipment Starting and Testing:	Section 23 08 23.

1.2	SUBMITTALS

.1	Product Data:

.1	Submit manufacturer’s product data in accordance with Section 20 00 13 – Mechanical General Requirements.

.2	Shop Drawings:

.1	Submit shop drawings in accordance with Section 20 00 13 – Mechanical General Requirements.

.1	Show on shop drawings equipment, piping and connections, valves, strainers thermostatic valves required for complete system.

.3	Closeout Submittals:

.1	Submit operations and maintenance data for incorporation into manuals specified in Section 20 01 06 – Mechanical Operation and Maintenance Manual.

1.3	QUALITY ASSURANCE

.1	Provide air cooled centrifugal water chiller[s], outdoor package type, prewired, factory assembled and products of manufacturer regularly engaged in production of unit of type and size specified, who issues complete catalogue data on such products.

.2	Manufacturer shall be responsible for selection and operation of components furnished by him.  Provide written certification that components not furnished by him have been selected in accordance with his requirements.

2.	Products

2.1	COMPRESSOR

.1	Design compressor casing such that excessive loads cannot be placed on shafts, bearings or seals during assembly or disassembly. Statically and dynamically balanced rotor shall have heat treated forged or rolled steel shaft and cast or built-up impellers made of or coated with corrosion or encrustation resisting material.

.2	Use babbitted sleeve main bearings. Provide compressor with force feed lubricating system arranged to ensure adequate lubrication during starting, stopping and normal operation conditions, and including automatic oil heater and cooler.

.3	Provide compressor with automatic capacity reduction equipment consisting of radial blade guide vanes at inlet making machine capable of continuous operation at minimum capacity of not more than 10% of specified capacity.

.4	Provide gear box, if required, of ample capacity, operating without excessive noise or vibration. Provide pressure lubrication with pump and cooler.

.5	Provide hermetically sealed compressor motor of induction type operating at 3600 r/min, designed for reduced voltage starting, free from vibration, and not exceeding maximum design torque of compressor or gear. Cool motor with refrigerant and seal electric terminals hermetically. Provide reduced voltage or wye-delta starter of closed transition type, causing motor to break away from rest and accelerate on first step.

2.2	EVAPORATOR

.1	Evaporator shall be shell and tube type. Use shells of welded steel construction, copper tubes with integral fins rolled or silver brazed into tube sheets. Provide tightly fitted tube supports along axis of shell. Provide multiple orifice refrigerant flow control to maintain pressure differential between condenser and evaporator.

.2	Provide water boxes of welded steel, arranged to permit inspection of tubes from either end without disturbing the refrigerant chamber, and removable without disturbing water piping.

2.3	CONDENSER

.1	House condenser components in heavy gauge galvanized steel casing  with weather resistant finish.

.2	Construct condenser coil of aluminum fins mechanically bonded to copper tubing. Provide sub-cooling circuit.

.3	Condenser fans shall be vertical discharge belt driven propeller type. Provide fan guard on discharge. Bearings shall be roller or ball type with grease fittings extended to outside of casing.

.4	Fan motor shall have permanently lubricated ball bearings and 3.1 built-in current and overload protection.

2.4	ENCLOSURES

.1	All components except condenser and starters shall be housed in galvanized steel, weathertight, insulated and heated equipment room.

.2	Mount starters and disconnects in separate weathertight enclosure provided with fully opening doors.  Provide mechanical interlock to disconnect system when door is opened.

2.5	CONTROLS

.1	Provide factory wired and mounted control panel inside equipment room.  Panel to incorporate all necessary refrigeration and electrical controls, including gauges for oil and refrigerant pressures, pump and fan switches, indicator lights, system switch and load limit controls.

.2	Starter and disconnect enclosure shall incorporate control power transformer, load limit relay current transformer, magnetic overload protection devices, safety circuits and starters for compressor, oil pump, and condenser fans.

3.	Execution

3.1	PERFORMANCE

.1	Provide [     ] air cooled packaged chiller[s], [each] having capacity of [     ]kW minimum of refrigeration when delivering [     ]L/s of chilled water at [     ]°C with air entering condenser at [     ]°C evaporator fouling factor not less than 0.0005, and power input of [     ]kW. Water head loss through [     ] - pass evaporator shall not exceed [     ]kPa.

.2	Unit[s] shall be [     ] Model [    -].

3.2	INSTALLATION

.1	Install chiller package on steel or concrete beams in accordance with manufacturers recommendations.

.2	Provide isolators between unit and structural support members to dampen vibration transmission.

.3	Provide initial charge of refrigerant and oil.

3.3	STARTING AND TESTING

.1	Start and test chillers as specified in Section 23 08 13 and 23 08 23.

END OF SECTION