Section Cover Page

Section 23 81 13 Packaged Terminal Air 2010-12-31 Conditioning Units

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if project: .1 is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Submittals

1.2	Quality Assurance

2.	Products

2.1	Type

2.2	Cabinet

2.3	Heating and Cooling Chassis

2.4	Controls

3.	Execution

3.1	Installation

3.2	Performance

LEED Notes:

Refer to Section 01 35 18 – LEED Requirements for:

1.	Requirements necessary for this project to obtain points required for certification.

2.	Confirmation of LEED prerequisites and credits affecting this Section; not all are mandatory for certification

Maintain built-in sustainability regardless of LEED requirements for:

.1	Recycling, reuse of materials, components and assemblies.

.2	Diversion of construction waste from landfills.

.3	Use of recycled materials, local materials, rapidly renewable and durable materials.

.4	Maintain healthy indoor environment during constructing.

.5	Provide for thermal comfort, access to views and daylight for indoor spaces.

.6	Foster innovation into facility design and planning.

LEED Credits:

Energy & Atmosphere

Prerequisite 2 – Minimum Energy Performance

Prerequisite 3 – Fundamental Refrigerant Management

Note:  Though prerequisites do not contribute to a projects point score, they are mandatory and MUST be met for a project to receive LEED Canada – NC certification.

Credit 1 – Optimize Energy Performance

Credit 4 – Enhanced Refrigerant Management

Note:  Chlorofluorocarbons (CFCs) are a class of chemicals used in refrigeration equipment that contribute to the destruction of the ozone layer.  Hydrochlorofluorocarbons (HCFCs) based refrigerants are more environmentally friendly than CFC based refrigerants but still have a high ozone depletion potential (OPD).  Energy and Atmosphere prerequisite 3 requires that LEED projects eliminate CFCs in all base building HVAC&R systems. Energy and Atmosphere credit 4 awards points for using HVAC and refrigeration equipment that is free of HCFCs.

Note: Whenever possible, the building should be designed to take advantage of passive heating and cooling systems. Strategies include, but are not limited to, a more efficient building envelope, operable windows, and building orientation.

1.	General

1.1	submittals

.1	Product Data:

.1	Submit manufacturer’s product data in accordance with Section 20 00 13 – Mechanical General Requirements.

.1	Submit type of refrigerant used.

.2	Shop Drawings:

.1	Submit shop drawings in accordance with Section 20 00 13 – Mechanical General Requirements.

.3	Closeout Submittals:

.1	Submit operations and maintenance data for incorporation into manuals specified in Section 20 01 06 – Mechanical Operation and Maintenance Manual.

1.2	QUALITY ASSURANCE

.1	Conform to requirements of CSA, Provincial and Municipal Codes.

.2	Units shall be product of manufacturer regularly engaged in production of these units and who issues complete catalogue data for same.

2.	Products

2.1	TYPE

.1	Provide packaged, self-contained, through-the-wall air cooled terminal air conditioning units, with [wall sleeve,] room cabinet, electric cooling, [electric] [hot water] heating, [outside air louvres,] [built-in] [remote] temperature controls.

2.2	CABINET

.1	Cabinet shall be [wall mounted] [floor mounted] [sub-base mounted] of heavy gauge steel with [epoxy coated] [baked enamel] finish and removable front panel.

.2	Top of cabinet shall incorporate integral discharge grille and access door for controls.

2.3	HEATING AND COOLING CHASSIS

.1	Removable unit chassis shall incorporate [electric] [hot water] heating coil, direct expansion cooling coil, compressor, centrifugal evaporator fan[s], [air cooled condenser fan and coil,] [water cooled condenser,] permanent filters, ventilation duct, dampers, and controls.

.2	Provide condensate drain pan under cooling coil with built-in re-evaporation system.

.3	Provide [separate motors] [common motor] to drive evaporator and condenser fans.

2.4	CONTROLS

.1	Supply units with [manual] [motorized] ventilation dampers, [built-in] [remote] heat-cool-off switch.

.2	Provide [single] [two] speed evaporator fan motor with built-in fan switch.

.3	Provide units with low ambient lockout control to prevent compressor operation below 35°C.

.4	Controls shall incorporate automatic change over from heating to cooling in response to room thermostat.

3.	Execution

3.1	INSTALLATION

.1	Coordinate installation of units with architectural and electrical trades.

.2	Supply units fully charged with refrigerant and oil.

3.2	PERFORMANCE

.1	Provide [      ] air cooled packaged through the wall terminal air conditioning unit[s] [each] having to total cooling capacity of [     ]kW and heating capacity of [     kW].

.2	Provide [     ] water cooled packaged through the wall terminal air conditioning unit[s] [each] having a heating capacity of [     ]kW and total cooling capacity of [     ]kW when supply with [     ]L/s condenser water entering at [     ]°C.

.3	Unit[s] shall be [     ] Model [     ].

END OF SECTION