Section Cover Page

Section 23 82 05 2010-12-31 Terminal Heat Transfer Units

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Submittals

1.2	Quality Assurance

2.	Products

2.1	General

2.2	Baseboard Radiation

2.3	Wall Fin Radiation

2.4	Convectors

2.5	Unit Heaters

2.6	Fancoil Units

2.7	Unit Ventilators

3.	Execution

3.1	Installation

3.2	Performance

3.3	Radiation and Convector Schedule

3.4	Cabinet and Unit Heater Schedule

1.	General

1.1	SUBMITTALS

.1	Shop Drawings:

.1	Submit shop drawings in accordance with Section 20 00 13 – Mechanical General Requirements.

.1	Submit, in addition to shop drawings, schedules of radiation heating elements and enclosure indicating length and number of pieces of element and enclosure, corner pieces, end caps, cap strips, access doors, pilaster covers and a comparison of specified heat  required to actual heat output provided.

1.1	QUALITY ASSURANCE

.1	Terminal heat transfer units shall be product of manufacturer regularly engaged in production of such units who issues complete catalogue data on such products.

2.	Products

2.1	GENERAL

.1	For each convection type heating unit not thermostatically controlled, provide knob-operated internal damper at enclosure air outlet grille. [Where group of rooms is zoned on one thermostat, provide dampers in each room].

.2	Factory apply baked primer coat on metal surfaces of enclosure or cabinet.

2.2	BASEBOARD RADIATION

.1	Heating Elements:  20 mm nominal copper tubing mechanically expanded into flanged collars of evenly spaced aluminum fins, one tube end belled.

.2	Enclosure:  Minimum 0.8 mm steel with back and top of one piece, front panel, end caps, corners and joiner pieces to snap together, front panel easily removable, full length damper.

.3	Element Brackets:  1.2 mm galvanized steel to support front panel and noise free element cradle.

2.3	WALL FIN RADIATION

.1	Heating Elements:  30 mm seamless copper tubing, 1 mm minimum wall thickness, mechanically expanded into evenly spaced aluminum fins, suitable for sweat fittings.

.2	Heat Elements:  30 mm condenser tube, 3 mm minimum wall thickness mechanically expanded into evenly spaced steel fins.

.3	Element Hangers:  Quiet operating, ball bearing cradle type providing unrestricted longitudinal movement, on enclosure bracket.

.4	Enclosures:  1.2 mm steel up to 450 mm in height, 1.6 mm steel over 450 mm in height c/w easily jointed components for wall to wall installation. Support rigidly, top and bottom, on wall mounted brackets at 900 mm centres maximum.

2.4	CONVECTORS

.1	Heating Elements:  Seamless copper tubing mechanically expanded into evenly spaced aluminum fins and cast iron heaters, steel side plates and supports, factory air pressure tested at 690 kPa under water, and means of adjusting pitch of element.

.2	Cabinet:  1.6 mm steel front and top, 1.2 mm steel back and ends, exposed corners rounded, easily secured removable front panels, adequately braced and reinforced for stiffness.

2.5	UNIT HEATERS

.1	Casing:  1.2 mm steel with threaded connections for hanger rods.

.2	Coils:  Seamless copper tubing, 0.6 mm minimum wall thickness, silver brazed to steel headers, and with evenly spaced aluminum fins mechanically bonded to tubing.

.3	Fan:  Direct drive propeller type, statically and dynamically balanced. Horizontal models complete with sleeve bearings and fan guard. Vertical model complete with grease lubricated ball bearings.

.4	Air Outlet:  Adjustable pattern diffuser on projection models and four-way louvers on horizontal throw models.

2.6	FANCOIL UNITS

.1	Cabinet:  1.6 mm steel with rounded exposed corners and edges, easily removed panels, glass fiber insulation [, and integral air outlet] [and inlet grilles].  [Finish exposed surfaces in baked enamel of approved colour].

.2	Coils:  Evenly spaced aluminum fins mechanically bonded to copper tubes, designed for maximum operating limits of 1380 kPa and 104°C.

.3	Fans:  Centrifugal forward curved double width wheels, statically and dynamically balanced, direct driven, on sleeve bearings resiliently mounted.

.4	Filter:  Easily removed 25 mm thick glass fiber throw-away or permanent washable type filtering air before coil.

.5	Control:  [4 position speed switch factory wired and CSA approved. [2 speed switch located in cabinet where accessible. Provide key operated wall mounted switch where inaccessible.

2.7	UNIT VENTILATORS

.1	Cabinet:  Fabricate of 2 mm furniture grade steel on solid base pan with exposed edges rounded and removable front panels with quick-acting, key-operated camlocks. Finish external surfaces in baked enamel of approved colour. Provide removable die-cast or fabricated steel discharge grilles. [With units having cooling coils, insulate internal parts and surfaces exposed to conditioned air stream with temperature and moisture resistant material].

.2	Fans:  Centrifugal forward curved double width wheels, statically and dynamically balanced, direct driven, on sleeve bearings resiliently mounted to draw air through coil. Manually control motor by key-operated on/off switch.

.3	Mixing Dampers:  Multi-blade with compressible seal capable of varying proportion of mixed air from 100% room air to 100% outside air.

.4	Filters:  Easily removed 25 mm thick glass fiber throw-away or permanent washable type, filtering air before unit coil.

.5	Outside Air Intake:  [Anodized aluminum] [Steel] wall intake box and louvers removable from frame with 12 mm square mesh galvanized screen in back of louver.

.6	Coils:  Copper tubes mechanically expanded into evenly spaced aluminum fins tested to operate at 1030 kPa. [Provide 1 gauge galvanized steel drain pan under cooling coil, easily removed for cleaning and with large drain connection].

.7	Wiring:  Factory installed, CSA approved.

3.	Execution

3.1	INSTALLATION

.1	Provide each unit with shut-off valve on supply and lockshield balancing valve on return piping.

.2	Provide each unit at high points with easily accessible manual air vent. If not easily accessible, extend vent to exterior surface of cabinet for easy servicing. For fan coil units and unit heaters provide float operated automatic air vents with stop valve.

.3	For inaccessible valves, provide factory-made permanently hinged access doors, 150 x 180 mm minimum size, integral with cabinet.

3.2	PERFORMANCE

.1	Refer to schedules.

.2	Radiation and convector capacities are based on 18°C entering air temperature, 82°C average water temperature.

.3	Unit heater and fancoil capacities are based on 16°C entering air temperature, 82°C entering water temperature.

3.3	RADIATION AND CONVECTOR SCHEDULE

Type

Manufacturer

Model

Enclosure

Rows

kW/m

Remarks

3.4	CABINET AND UNIT HEATER SCHEDULE

Unit No.

Location

Service

Manufacturer

Model

kW

L/s

Motor r/min

Motor kW

Remarks

END OF SECTION