Section Cover Page

Section 23 82 26 2010-12-31 Induction Units

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Mockup

2.	Products

2.1	Materials

2.2	Fabrication

3.	Execution

3.1	Installation

3.2	Performance

1.	General

1.1	MOCKUP

.1	Assemble mockup installation of one typical bay, under window enclosure assembly complete with induction units at site prior to manufacturer of enclosures. Complete assembly subject to approval of the Minister.

2.	Products

2.1	MATERIALS

.1	Base Unit Casing:  1.0 mm minimum galvanized steel.

.2	Nozzles:  Heat resistant plastic suitable for temperatures from -29°C to 93°C with 0.87 kPa nozzle pressure.

.3	Water Coil:  One row, 15 mm OD copper tubing with aluminum fins.

.4	[Drainable] [Non-Drainable] Drain Pan:  1.0 mm minimum galvanized steel.

.5	Lint Screens:  Aluminum mesh.

.6	Cabinet Enclosures:  Thickness 1.2 mm - 1.6 mm.

.7	Discharge Grilles:  Plastic, cast metal or stamped steel.

2.2	FABRICATION

.1	Base unit shall include acoustically insulated primary air plenum, primary air inlets, internal air damper, induction nozzles, water coil, lint screen, drain pan. Provide interchangeable transition pieces or plugs as required for single or series hook up.

.2	Spot weld and seal joints in base unit. Paint portion of unit visible through discharge opening with flat black enamel.

.3	Fabricate internal primary air damper of multiple orifice design manually adjustable from under discharge grille.

.4	Fabricate cabinet enclosures complete with mounting channels, end trim pieces, mullion spacers, removable front panels, removable discharge grilles. Fabricate enclosures to cover induction units and be continuous column to column or wall to wall.

3.	Execution

3.1	INSTALLATION

.1	Provide manual air vents on coil return pipe and radiator valves on both supply and return piping. Provide piping configuration as indication on drawings only.

.2	Connect drain pan to condensate drain.

.3	Support base units from continuous wall mounting strip or wall mounting brackets. Support cabinet enclosures from wall mounting strip or attach direct to wall and floor.

3.2	PERFORMANCE

.1	Induction units shall be [     ] type [     ] Model [     ] of size, configuration and capacity as shown on the drawings.

END OF SECTION