Section Cover Page

Section 23 84 15 2010-12-31 Evaporative Humidifier

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Quality Assurance

1.2	General Requirement

1.3	Submittals

2.	Products

2.1	Materials

2.2	Products

3.	Execution

3.1	Preparation

3.2	Installation

3.3	Performance

1.	General

1.1	QUALITY ASSURANCE

.1	Product of manufacturer regularly engaged in production of such units who issues complete catalogue data on such products.

1.2	GENERAL REQUIREMENT

.1	Provide units consisting of casing, tank, filters, spray pumps, water and drain connections.

.2	Factory assemble units prior to shipment.

1.3	SUBMITTALS

.1	Product Data:

.1	Submit manufacturer’s product data in accordance with Section 20 00 13 – Mechanical General Requirements.

.2	Shop Drawings:

.1	Submit shop drawings in accordance with Section 20 00 13 – Mechanical General Requirements.

.1	Indicate project layout, dimensions and extent of humidification system.

.3	Closeout Submittals:

.1	Submit operations and maintenance data for incorporation into manuals specified in Section 20 01 06 – Mechanical Operation and Maintenance Manual.

2.	Products

2.1	MATERIALS

.1	Casing: Galvanized steel, reinforced and braced with galvanized angle iron.  Provide with adhesive backed neoprene gasket and one quick opening access door.

.2	Drain Tank:  3.5 mm welded black steel, prime coated inside and out with zinc chromate, iron oxide, phenolic resin paint.

.3	Filters:  [Two rows (wet and dry) of rubberized filters in removable frames].  [Cellulose flute bonded with acrylic adhesive].

.4	Water Inlet:  Float valve assembly with brass rod, float ball and valve; with replaceable neoprene seat.

.5	Spray Pumps:  [Centrifugal pump with brass impeller and cut-off blade, in galvanized well; built-in overload protection].  [Refer to pump section].

.6	Distribution System:  PVC piping.

2.2	PRODUCTS

.1	Gasket and flange pipe penetrations, inspection panels, access doors and other openings in unit casing.

.2	Fabricate drain tank with corners lapped and welded watertight.  Weld fittings and piping supports to tank.  Provide fittings, suitably sized, for water make-up, 20 mm hose bibb, drain and overflow.

.3	Provide water make-up with adjustable float valve, easily removable drain and overflow to prevent escape of air and water during operation, and float operated low water cut-off to stop spray pump.  Provide hose bibb accessible from interior.

3.	Execution

3.1	PREPARATION

.1	Paint interior surfaces with two coats of zinc rich paint applied after assembly.

3.2	INSTALLATION

.1	Place unit on neoprene coated cork pad same size as unit tank.  Flash and counterflash with 1.0 mm galvanized iron entering and leaving sides to eliminate exposure of the cork to water.

.2	Provide 12 mm bleed line from sump drain to nearest floor drain complete with globe valve and solenoid valve.

.3	Bolt spray pump directly to tank fitting.

.4	Insulate exterior of unit same as specified for ductwork.

3.3	PERFORMANCE

.1	Provide [     ] evaporative humidifier [     ] Model [     ] suitable for [     ]L/s with maximum air pressure drop [     ]kPa saturation efficiency minimum [     ]%.

END OF SECTION