Section Cover Page

Section 26 05 53 Identification 2017-01-30 for Electrical Systems

Use this Section to specify all requirements related to identification of electrical equipment, systems, wiring g, conduit and cable, pull and junction box covers and other electrical work.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Data Sheet - General

.3	Data Sheet - Communications Cable and Equipment Labeling Method

.4	Specification Section Text:

1.	General

1.1	Related Sections

1.2	Reference Documents

2.	Products

2.1	Identification Materials

3.	Execution

3.1	Colour Identification of Equipment

3.2	Nameplate Identification of Equipment

3.3	Panelboard Directories

3.4	Communications Cable and Equipment Labeling

3.5	Intermittent Colour Coding of Conduit and Cable

3.6	Identification of Pull and Junction Boxes

3.7	Colour Identification of Wiring

3.8	Name/Number Identification of Wiring

3.9	Identification of Receptacles and Fire Alarm End-of-Line Resistors and Duct Detectors

3.10	Equipment Identification Schedule

This Section makes specific references to numerous items of equipment and systems, not all of which will apply to every project.  Edit this Section accordingly to delete inapplicable requirements.

Identification and labeling, including colour coding of conduit and cable, is the responsibility of the electrical subcontractor.  The painting subcontractor is responsible for onsite painting of electrical conduit, cable and equipment, excluding banding.  Identification requirements are specified accordingly in this Section and in Section 09 91 30 - Painting of Mechanical and Electrical Work.

Use the following identification standard when labeling communications cabling components.  Include required cabling designations on the drawings.

IDF Rooms Number:  XYZ, where:

-	"XY" is floor number represented by two digits.

-	"Z" is a sequential letter (A,B, etc.) designating which room.  Riser and equipment rooms are considered equivalent.

Outlet Assembly:  000-X where:

-	"000" is a three-digit address.

-	"X" is one of following outlet types:

-	"A" for telephone outlet.

-	"B" for data (copper) outlet.

-	"C" for data (fiber) outlet.

Panels:

.1	Horizontal Distribution:  XYZ-H, where:

-	"XYZ" is room number as described above.

-	"-H" indicates "Horizontal".

-	Port Labeling:  three-digit address of workstation connected.

.2	Equipment:  XYZ-E

-	"XYZ" is room number as described above.

-	"E" indicates "Equipment".

-	Port Labeling:  three-digit sequential number

.3	Riser:  XYZ-R

-	"XYZ" is room number as described above.

-	"R" indicates "Riser".

-	Port Labeling:  three-digit sequential number

.4	RS-232/422:  XYZ-RS[232][422]:

-	"XYZ" is room number as described above.

-	Port Labeling:  two-digit sequential number.

.5	Attach inter-room connection to identically numbered panel outlets, and, wherever possible, to outlets at same position on each panel.

Cables:

.1	Horizontal (outlet) Cables:

.1	Outlet End:  XYZ, where "XYZ" designates IDF room number as described above to which cable goes.

.2	Room (IDF) End:  PQR-[OUTLET TYPE], where:

-	PQR is a three-digit outlet address,

-	[OUTLET TYPE] is one of the following outlet types:

-	A for telephone

-	B for data

-	C for fiber

-	RS-232

-	RS-422

.3	Equipment Room/Riser/Backbone Cables: destination is another IDF room, MDF room, or outlet.

TYPE-[MN]/[XYZ][[0][00]] where:

-	[TYPE] would be:

-	VUTP for (voice UTP).

-	DUTP for (data UTP).

-	DSTP for (data STP).

-	FO for (fiber optic).

-	COAX (coaxial).

-	RS[232][422]

-	[MN] is sequential number (01, 02, etc.) of cable if multiple runs of same type.

-	XYZ is IDF Or MDF destination room if cable goes to another IDF or MDF room

-	[0]00  is the address of the outlet if cable goes to outlet.

# END OF DATA SHEETS

1.	General

1.1	scope

.1	Identification for electrical systems, equipment, conduit and related components.

1.2	RELATED SECTIONS

.1	Submittals	Division 01

.2	Painting of Mechanical and Electrical Work	Section 09 91 30

1.3	quality control

.1	Coordinate painting of electrical work with Section 09 91 30.

.2	Colour code electrical equipment, components and exposed conduits.

.3	Submit a schedule of conduit and equipment identification methods, materials and colours to the Minister’s representative for review.

1.4	Reference standards

.1	Federal Standard 595C Colours.

2.	Products

2.1	IDENTIFICATION MATERIALS

.1	Lamicoid Nameplates: 3 mm thick plastic engraving sheet, black face, white core, mechanically attached, sizes as follows:

.1	Size 1:  12 mm high with 5 mm high letters.

.2	Size 2:  20 mm high with 8 mm high letters.

.3	Size 3:  25 mm high with 12 mm high letters.

.2	Wire Identification Materials:  Use one of the following:

.1	Heat shrink sleeves, blank.

.2	Clear plastic tape wrap-on strips with white writing section.

.3	Wrap-on strips, pre-numbered.

.4	Slip-on identification bead markers or sleeves, blank or pre-numbered.

.3	Colour Banding Tape:  25 mm wide adhesive backed plastic tape, integrally coloured.

3.	Execution

3.1	COLOUR IDENTIFICATION OF EQUIPMENT

.1	Electrical equipment shall be prefinished in coded colours designating voltage or system, as indicated.

SPEC NOTE:  Edit 3.1.2 and 3.1.3 to delete inapplicable voltages and systems.

.2	All switchgear, distribution centre, panel boards, motor control centre, motor starter cabinets, motor control cabinets, disconnect switches, contractor cabinets, relay cabinets, transformers, termination cabinets, splitter boxes, busduct, cable duct, etc., are to be color coded as follows:

Voltage	Colour

.1	High Voltage (in excess of 750 V):	Brown

.2	347/600 V:	Sand

.3	120/208 V:	Grey

.4	Emergency Power:	Associated Voltage Colour

.5	Fire Alarm & Firephone:	Red

.6	Security/Intrusion/Surveillance:	Green

.7	Low Voltage Switching:	Black

.8	Annunciator Cabinets:	Black

.9	Data/Telephone Cabinets:	Blue

.10	Telephone Backboards:	Grey

.11	Television:	White

.12	Public Address/Intercom:	Purple

.3	All pull boxes, junction boxes, covers, and conduit banding shall be finished in the following colors:

System	Colour

.1	347/600 V:	Sand

.2	347/600 V Emergency:	Sand (covers marked “EM”)

.3	277/480 V:	Bronze

.4	277/480 V Emergency:	Bronze (covers marked “EM”)

.5	120/208 V:	Grey

.6	120/208 V Emergency:	Grey (covers marked “EM”)

.6	In Excess of 750 V:	Brown

.7	In Excess of 750 V – Emergency:	Brown (covers marked “EM”)

.8	Fire Alarm & Firephone:	Red

.9	Security/Intrusion/Surveillance:	Green

.10	Data/Telephone (VOIP):	Blue

.11	Public Address/Intercom:	Purple

.12	Sound Masking:	Orange

.13	Nurse Call:	Yellow

.14	Television:	White

.15	Low Voltage Switching:	Black

.16	Low Voltage Switching – Emergency:	Black (covers marked “EM”)

Note:	All cover markings are to be in “Black” lettering with the exception of Low Voltage Switching – Emergency that is to be marked with “White” lettering.

.4	Where impracticable to obtain equipment prefinished in coded colours, equipment may be site painted in coded colours.  Coordinate with work specified in Section 09 91 30.

3.2	NAMEPLATE IDENTIFICATION OF EQUIPMENT

.1	Identify equipment with lamicoid nameplates, as indicated in Equipment Identification Schedule.

3.3	PANELBOARD DIRECTORIES

.1	Identify loads controlled by each overcurrent protective device in each panelboard, by means of a typewritten panelboard directory.

3.4	COMMUNICATIONS CABLE AND EQUIPMENT LABELING

.1	Label communication outlets, panels and ports with lamicoid nameplates as specified in Equipment Identification Schedule.

.2	Label each of cables with other ends address using Wire Identification Materials.

.3	Label outlets with labels vertically aligned in each row.

.4	Position panel labels in the same position on each panel.

3.5	INTERMITTENT COLOUR CODING OF CONDUIT AND CABLE

.1	Apply colour banding (tape or paint) in required colours for each voltage or system in 25 mm wide bands all around conduit or cable as follows:

.1	At least once in each 10 m of conduit or cable run.

.2	Where conduit or cable enters inaccessible ceiling, wall and floor spaces.

.3	At least once in each room or area through which a conduit or cable passes.

.2	Apply colour banding on electrical conduit and cable in the following locations as defined in Section 09 91 30:

.1	Exposed in service areas.

.2	Exposed in unfinished areas.

.3	Semi-concealed spaces.

.4	Exposed to Exterior.

3.6	IDENTIFICATION OF PULL AND JUNCTION BOXES

.1	Identify pull and junction boxes over 100 mm size as follows:

.1	Use boxes which are prefinished in coded colours, or spray paint inside and outside of boxes prior to installation, in coded colours designating voltage or system.

.2	Apply size 2 lamicoid nameplate to cover of each box.  Identify system name.  Where sequence identification is required, identify system name and number.

.2	Identify pull and junction boxes 100 mm or less in size as follows:

.1	Spray paint inside of boxes in coded colours designating voltage or system.

.2	Apply permanent identifying markings directly to box covers designating voltage or system using indelible black ink.

3.7	COLOUR IDENTIFICATION OF WIRING

.1	Identify No. 4/0 AWG wiring and smaller by continuous insulation colour.

.2	Identify wiring larger than No. 4/0 AWG by continuous insulation colour or by colour banding tape applied at each end and at splices.

.3	Colour coding shall be in accordance with Canadian Electrical Code, and as follows:

|  | Voltage | Colour |
| --- | --- | --- |
| .1 | 120/208 V, 3 phase: | Red, black and blue. |
| .2 | 120/208 V emergency: | Red, black and blue with |
|  |  | yellow tracer. |
| .3 | 347/600 V 3 phase: | Orange, brown and yellow. |
| .4 | 347/600 V emergency: | Orange, brown and yellow |
|  |  | with red tracer. |

.4	Where multi-conductor cables are used, use same colour coding system for identification of wiring throughout each system.

.5	Maintain phase sequence and colour coding throughout each system.

3.8	NAME/NUMBER IDENTIFICATION OF WIRING

.1	Identify No. 8 AWG wiring and smaller using one of the wire identification materials specified in 2.1.

.2	Type or print on blank wire identification materials using indelible black ink.

.3	Identify wiring at all pull boxes, junction boxes, and outlet boxes for all systems.

.4	Identify each conductor as to panel and circuit, terminal, terminal numbers, system number scheme, and polarization, as applicable.

3.9	IDENTIFICATION OF RECEPTACLES AND FIRE ALARM END-OF-LINE RESISTORS AND DUCT DETECTORS

.1	Standard duplex receptacles: provide lamicoid nametag with 6 mm high white lettering on black background (red background for emergency receptacles) indicating circuit and panel designation and locate on wall above receptacle. On all other receptacles provide lamicoid nametag indicating voltage, phase, amps, circuit and panel designations.

.2	Fire alarm end-of line resistors and duct detectors: identify zone number with 6 mm high white lettering on red background on lamicoid nametag located on wall above device. Identify remote LED indicators for duct detectors.

SPEC NOTE:  Edit "Equipment Identification Schedule" to delete inapplicable items of equipment and identification requirements.

3.10	EQUIPMENT IDENTIFICATION SCHEDULE

| Equipment | Colour | Nameplate Identification | Lamicoid Nameplate Size |
| --- | --- | --- | --- |
| Main Distribution Centre | Voltage Colour | - Building name, consulting engineer, date installed, amperage, voltage | 3 |
|  |  | - Main breaker Metering cabinet | 2 |
|  |  | - Instrument transformer enclosure | 2 |
|  |  | - Loads controlled by each overcurrent protective device | 1 |
|  |  | - Metering devices | 1 |
| Distribution Centres | Voltage Colour | - Distribution centre designation, amperage, and voltage | 2 |
|  |  | - Loads controlled by each overcurrent protective device | 1 |
| Panelboards | Voltage Colour | - Panelboard designation | 2 |
| Motor Control Centres | Voltage Colour | - M.C.C. designation, amperage and voltage | 2 |
|  |  | - Motors or loads controlled by each unit and mnemonics | 1 |
|  |  | - Relay terminal and transformer compartments | 1 |
| Manual Motor Starters | N/A | - Load controlled and mnemonics | 1 |
| Ground Bus | N/A | - System Ground | 1 |
| On/Off Switches | N/A | - Load controlled | 1 |

cont'd

3.10	EQUIPMENT IDENTIFICATION SCHEDULE (Cont'd)

| Equipment | Colour | Nameplate Identification | Lamicoid Nameplate Size |
| --- | --- | --- | --- |
| Disconnect | Voltage | - Voltage and equipment | 2 |
| Switches, | Colour | controlled and mnemonics |  |
| Magnetic |  |  |  |
| Motor Starters |  |  |  |
| and Contactors: |  |  |  |
| Transformers | Voltage Colour | - Transformer designation, capacity, secondary and primary voltages | 2 |
| Emergency Power Equipment | Voltage Colour | - Designation and voltage | 2 |
| Wireways | N/A | - Voltage and system designation | 2 |
| Line Voltage | Voltage | - Designation and voltage | 2 |
| Cabinets and | Colour |  |  |
| Enclosures |  |  |  |
| Low Voltage Cabinets and | System Colour | - System name; system name and number if more than one cabinet or enclosure | 2 |
| Enclosures |  | - Major components within cabinets and enclosures | 1 |
| Communication |  |  |  |
| Outlet and |  |  |  |
| Outlet |  |  |  |
| Assemblies | N/A | - Outlet Designation | 1 |
| Communication |  |  |  |
| Panels | N/A | - Panel Designation | 1 |
| Communication |  |  |  |
| Ports | N/A | - Port Designation | 1 |

3.11	COLOUR SCHEDULE

Federal Standard 595C

Electrical Colours		Colour Numbers

Blue	15052

Green	14449

Brown	10115

Sand	13613

Grey	16307 or ASA61 Grey

Black	17038

Bronze	13275

Purple	17100

Orange	12473

Yellow	13655

Red	11350

## END OF SECTION