Section Cover Page

Section 26 08 10 Electrical Starting and Testing 2018-06-12 - General Requirements

Use this Section to specify general requirements for electrical starting and testing.  Use this section in conjunction with the following:

Section 26 08 20	Electrical Starting and Testing by Contractor

Section 26 08 30	Electrical Starting and Testing by Contractor's Testing Agent

Do not specify electrical starting and testing requirements in individual technical sections; include cross-references to this Section 26 08 10 only.

This Section contains:

.1	This Cover Sheet

.2	Data Sheet – Reference Documents

.3	Data Sheet - Test Report Forms

.4	Specification Section Text:

1.	General

1.1	Intent

1.2	Related Requirements

1.3	Reference Documents

1.4	Submittals

1.5	Start-Up Reports

1.6	Reports

1.7	Starting and Testing - General

1.8	Witnessing of Starting and Testing

1.9	Manufacturer's Starting Recommendations

1.10	Manufacturer's Service on Site

1.11	Reference Documents

1.12	Contractor and Manufacturer Reports

1.13	Correction of Deficiencies

1.14	Contractor's Testing Agent(s)

1.15	Fire Alarm System Testing and Verification

1.16	Province’s Independent Commissioning Authority

1.17	Coordination

1.18	Implementation

1.19	Scheduling

2.	Products

2.1	Test Equipment

3.	Execution

Not Used

The following Contractor Start-Up Program test report forms are available. Contact the Alberta Infrastructure Mechanical Section for the most up to date list of report forms.

Medium Voltage Power Distribution System (750 V – 69 KV)

.1	Distribution Switchgear

.2	Power Circuit Breaker

.3	Disconnect Switchgear

.4	Induction Disc Protective Relay

.5	Dry Type Transformer

.6	Liquid Filled Transformer

.7	Power Cable

.8	Current Transformer

.9	Potential Transformer

.10	DC Hi-Pot Test

.11	Protection Circuit DC Resistance Test

Normal Power Distribution System (Below 750 V)

.12	Main Distribution Switchgear

.13	Distribution Switchgear - Air Circuit Breaker

.14	Distribution Switchgear - Molded Case Breaker

.15	Solid State Overcurrent Relay

.16	Ground Fault Relay

.17	Grounding System Resistance Test Results

.18	Dry Type Transformer - 225 KVA and Above

.19	Dry Type Transformer - Below 150 KVA and Below

.20	Bus Duct

.21	Distribution Panel CDP

.22	Panelboard

.23	Panelboard with Contactor in Mains

.24	Room Data - Wiring Devices

.25	Exterior Receptacles and Vehicle Plug-in Pedestals

.26	Load Balance, Voltage and Power Factor Test Results

.27	Power Factor Correction Capacitor

Emergency Power Distribution System

.28	Emergency Generator Set

.29	Generator Set Control Panel

.30	Generator Site Test Record Form

.31	Transfer Switch

.32	Uninterruptable Power Supply (UPS) System

.33	Central Battery

Motor Control System

.34	Motor Control Centre

.35	Single Phase Motor and Starter

.36	Three Phase Motor and Starter

.37	Elevator and Control Equipment

Branch Circuit Wiring in Patient Care Areas

.38	Voltage Drop & Receptacle Tests

.39	Conductor Insulation Integrity & Breaker Tests

.40	Grounding Point Potential Difference Test

.41	Ground Return Path Voltage Rise Test

Fire Safety Systems

.42	Fire Alarm System Pre-Verification Check List

Lighting Systems

.43	Room Data - Interior Lighting

.44	Low Voltage Switching System

.45	Exterior Lighting and Controls

Communication and Security Systems

.46	Cable Television

.47	Wired Radio and Paging System

.48	Nurse Call System

.49	Pocket Page System

.50	Staff Alert System

.51	Video Surveillance

.52	Doctors/Staff Register System

.53	Intercom System

.54	Clock and Program System

.55	Sound Masking System

.56	Dictation System

.57	Telephone System

.58	Computer System

Security Systems

.59	Room Data - Interior Lighting

.60	Low Voltage Switching System

.61	Exterior Lighting and Controls

END OF DATA SHEETS

1.	General

1.1	INTENT

.1	This Section specifies general requirements common to all starting and testing of electrical equipment and systems.  Read this Section in conjunction with related Sections which specify specific portions of electrical starting and testing work.

.2	Except where otherwise specified, arrange and pay for the testing and related requirements specified in this and related Sections.

.3	If test results do not conform with applicable requirements, repair, replace, or adjust or balance equipment and systems.  Repeat testing as necessary until acceptable results are achieved.

1.2	RELATED Requirements

.1	Electrical Operation and Maintenance Data:	Section 26 01 10.

.2	Electrical Operation and Maintenance Manuals:	Section 26 01 11.

.3	Electrical Starting and Testing by Contractor:	Section 26 08 20.

.4	Electrical Starting and Testing by Contractor's Testing Agent:	Section 26 08 30.

.5	Electrical Equipment and Systems Demonstration and Instruction:	Section 26 08 40.

1.3	Reference Documents

.1	American National Standards Institute/InterNational Electrical Testing Association (ANSI/NETA)

| .1 | ATS 2009 | Standard for Acceptance Testing Specifications for Electrical Power Equipment and Systems |
| --- | --- | --- |

.2	Canadian Standards Association (CSA)

| .1 | CSA Z32 | Electrical Safety and Essential Electrical Systems in Health Care Facilities |
| --- | --- | --- |
| .1 | CSA Z462 | Workplace Electrical Safety |
| .1 | CSA C282 | Emergency Electrical Power Supply for Buildings |

.3	Underwriters Laboratories of Canada (ULC)

| .1 | CAN/ULC S524 | Installation of Fire Alarm Systems |
| --- | --- | --- |
| .2 | CAN/ULC S536 | Inspection and Testing of Fire Alarm Systems |
| .3 | CAN/ULC S537 | Verification of Fire Alarm Systems |
| .4 | CAN/ULC S1001 | Integrated Systems Testing of Fire Protection and Life Safety Systems |

1.4	SUBMITTALS

.1	Submit to the Province a list of equipment and instruments which will be used in starting, testing, balancing and adjusting electrical equipment.  The Province may require changes to the proposed equipment and instruments.

1.5	START-UP REPORTS

.1	Prepare Start-Up report using forms available from the Province.

.2	Where forms are not available from the Minister for specific systems or equipment, prepare appropriate forms.

.3	Submit Start-Up reports as part of Operation and Maintenance Manual specified in Section 26 01 11.

1.6	REPORTS

.1	Submit Contractor Start-Up Report forms in accordance with Section 01 33 35 documenting starting and testing procedures performed, and observed tests results obtained.

.2	Submit field reports in accordance with Section 26 01 10.

1.7	STARTING AND TESTING - GENERAL

.1	Prior to testing ensure all electrical equipment is cleaned and free of dust.

.2	After testing, protect equipment subject to dust from construction activities.

.3	Notify Province when starting and testing of all systems has been completed.

.4	Do not conceal or cover equipment until inspected, tested and approved by Province.

.5	Assume all liabilities associated with starting, testing and balancing procedures.

.6	Assume all costs associated with starting, testing, adjusting and balancing, including supply of testing equipment and witnessing of factory testing by Contractor and Province.

1.8	WITNESSING OF STARTING AND TESTING

.1	Prior to starting and testing of electrical equipment or systems, prepare a schedule of all tests specified.  Review schedule with the Province.

.2	Provide sufficient notice (minimum three days) prior to commencing tests requiring witnessing by the Province, or Province’s Independent Commissioning Authority.

.3	Province or Province's Independent Commissioning Authority may witness all or any portion of testing and starting procedures performed by Contractor or Contractor's Testing Agent.

.4	Contractor shall be present for all tests specified in Section 26 08 30.

1.9	MANUFACTURER'S STARTING RECOMMENDATIONS

.1	Prior to starting equipment or systems, obtain and review manufacturer's installation, operation and starting instructions.  Read in conjunction with procedures specified in Sections 26 08 20 and 26 08 30.

.2	Use manufacturer's and supplier's starting personnel where required to maintain validity of manufacturer's warranty.  Confirm with manufacturer that all testing specified in this Section and Sections 26 08 20 and 26 08 30 will not void any warranties.

.3	Compare installation to manufacturer's published data and record discrepancies.  Modify procedures detrimental to equipment performance prior to starting equipment.

1.9	MANUFACTURER'S SERVICE ON SITE

.1	Arrange and pay for qualified manufacturer's representatives to supervise starting and testing of following electrical equipment and systems:

.1	Automatic Power Factor Correction Equipment.

.2	Uninterruptable Power Supply (UPS) System.

.3	Sound Masking System.

.4	Doctor's/Staff Register System.

.5	Staff Alert System.

.6	Clock and Program Equipment.

.7	Dictation System.

.8	Intercom System.

.9	Sound System.

.10	Closed Circuit Television System.

.11	Cable Television.

.12	Security System.

.13	Emergency Generator Set and Control Panel.

.14	Emergency Voice Communication System.

.15	Fire Alarm System.

.16	HID Dimming System.

.17	Nurse Call System.

.18	Pocket Page System.

.19	Transfer Switch.

.20	Solar Photovoltaic System.

.21	[                    ].

.2	Manufacturer's personnel shall be experienced in design and operation of equipment and systems being started and have ability to interpret results of readings, and tests and report results in a logical fashion.

1.11	REFERENCE DOCUMENTS

.1	Perform tests in accordance with:

.1	These Contract Documents.

.2	Requirements of authorities having jurisdiction.

.3	Manufacturer's published instructions.

.4	Applicable CSA, IEEE, IPCEA, EEMAC, NEMA and ASTM standards.

.2	If requirements of any of the foregoing conflict, notify Minister before proceeding with tests and obtain clarification.

1.12	CONTRACTOR AND MANUFACTURER REPORTS

.1	Log and tabulate test results on appropriate test report forms provided by the Minister.

.2	Submit completed test report forms immediately after tests are performed.

.1	Record all data gathered on site on approved test report forms.

.2	Note any damage, missing parts or incomplete work on test form.

.3	Record date of corrected deficiencies on form.

.4	Arrange for Minister to initial completed test report forms prior to the end of the work day that information is gathered.  Provide the Minister with one photo copy of each completed test report form.

.5	Maintain one photocopy on site of all data taken during starting and testing period.

.6	Maintain one copy of all final starting, testing, balancing and adjusting reports on site up to interim acceptance of the work for reference purposes.

.3	Arrange for manufacturer to submit copies of all production test records for production tests required by EEMAC and CSA standards for manufactured electrical equipment to the Minister prior to shipping.

.4	Arrange for manufacturer to submit brief step-by-step description of entire starting procedure to allow Minister to repeat starting at any time.

1.13	CORRECTION OF DEFICIENCIES

.1	Correct all contract deficiencies found during electrical starting and testing of equipment and systems and Minister's performance verification.

1.13	CONTRACTOR'S TESTING AGENT(S)

.1	Arrange and pay for services of testing agent(s) to perform tests and verifications specified in Section 26 08 30 - Electrical Starting and Testing by Contractor's Testing Agent.

.2	Contractor's Testing Agent(s) Qualifications:

.1	Registered testing firm whose normal day to day business is electrical testing.

.2	Testing agent shall be independent of any Supplier, Contractor or Subcontractor who's work is tested and shall not have any financial or other interests in or with the Contractor.

.3	Minimum of five years experience in the maintenance and testing of electrical equipment and systems at all voltage levels up to and including 25 KV class.

.4	Employ at least one electrician holding a current journeyman's certificate in the Province of Alberta.

.5	Personnel involved in power system testing shall have proven experience in the use of the following test equipment:

.1	Meggers 250 volts, 1000 volt and 2500 volt.

.2	DC hipot test equipment up to 100 kV DC.

.3	Capacitance bridges.

.4	Transformer ratio test equipment.

.5	Contact resistance testers (ductor).

.6	Protective relay test equipment of current injection type for testing and calibration of induction disc and solid state protective devices.

.6	Testing Agent involved in testing of hospital wiring systems shall have proven experience in testing of branch circuit wiring in Patient Care areas as specified in CAN/CSA-Z32 "Electrical Safety in Patient Care Areas".

.3	Contractor's Testing Agent(s) Report:

.1	Arrange for Contractor's Testing Agent(s) to submit three bound copies of all test results, together with deficiency lists, and summary of tests, and include recommendations for any corrective action required directly to the Minister.

1.15	FIRE ALARM SYSTEM TESTING AND VERIFICATION

.1	The electrical design consultant will be responsible to perform and direct verification of fire alarm system in accordance with:

.1	CAN/ULC-S537, "Verification of Fire Alarm System Installations", and

.2	Alberta Labour General Safety Services Division, "Fire Alarm Systems Manual, Rev. 8", and

.3	Requirements of authority having jurisdiction.

.2	Contractor requirements in testing and verification of the fire alarm system are specified in Section 26 08 20 "Electrical Starting and Testing By Contractor".

1.16	Province’s independent commissioning authority (ICA)

.1	The Province may arrange for services of a ICA to witness, separately test or retest electrical equipment or systems.

.2	ICA may witness any or all tests or start-ups which are the responsibility of the Contractor as specified in Sections 26 08 20 - Electrical Starting and Testing by Contractor and Section 26 08 30 - Electrical Starting and Testing by Contractor's Testing Agent

.3	Commissioning of any system by the Province does not reduce the Contractors obligations for complete testing and start-up of systems as specified.

1.17	COORDINATION

.1	Coordinate starting of electrical equipment and systems with testing and demonstration and instruction of:

.1	Electrical equipment and systems specified in Division 26, 27 & 28.

.2	Mechanical equipment and systems specified in Division 20 to 23.

.3	Other equipment and system specified in other Divisions.

.2	Where any equipment or systems requires testing prior to starting, ensure that such work has been completed prior to starting of electrical equipment and systems.

1.18	SCHEDULING

.1	Provide a contractor start-up schedule as specified in Division 01.

2.	Products

2.1	TEST EQUIPMENT

.1	Provide all equipment and tools necessary to perform testing specified and as otherwise required.

3.	Execution

Not Used

END OF SECTION