Section Cover Page

Section 31 21 13 2018-06-06 Radon Mitigation Rough-in System

Use this Section to specify a radon mitigation rough-in system, as listed below.

The radon mitigation rough-in system is to be designed, inspected, photographed and tested by a Canadian National Radon Proficiency Program (C-NRPP) Certified Mitigation Professional, obtained by the Prime Consultant.

Alberta Infrastructure has mandated the rough-in system in new Government of Alberta owned and supported permanent buildings, with the qualification that our department be open to alternative solutions proposed by the Certified Mitigation Professional. The “rough-in” is considered the benchmark. A roughed-in suction pit and cage sub-slab depressurization method is to be used for the system.

Edit, remove from or add to this Section in consultation with Alberta Infrastructure - Technical Services Branch - Building Environment Unit specialists in radon control procedures (Phone: 780-422-7472, 780-422-7600 and 780-422-7440).

This Master Specification Section contains:

.1	This Cover Page

.2	Specification Section Text:

1.	General

1.1	Intent

1.2	References

1.3	Administration Requirements

1.4	Delivery, Handling and Storage

1.5	Environmental / Site Conditions

1.6	System Design Alternatives

1.7	Warranty

1.8	Performance Requirements

1.9	C-NRPP Inspection Requirements

2.	Products

2.1	Manufacturer

2.2	Geotextile Fabric

2.3	Gas Permeable Venting Layer

2.4	Membrane Barrier System

2.5	Suction Pit and Cage

2.6	Collection Pipe Extensions from the Suction Pit and Cage

3.	Execution

3.1	Installation

1	General

1.1	INTENT

- This section describes the minimum requirements for the supply and installation of a radon mitigation rough-in system.

- The radon rough-in system is to be designed, inspected, photographed and tested by a Canadian National Radon Proficiency Program (C-NRPP) Certified Mitigation Professional, obtained by the Prime Consultant.

- If, after the building is completed and occupied, long term radon testing results indicate the rough-in system needs to be activated, the installed components provide radon gas extraction points from within the building. Follow Health Canada guidelines for long term radon testing. The Building Owner would need to retain and pay for a (C-NRPP) Certified Mitigation Professional to conduct a feasibility test, to extend the extraction points to the outside of the building and mechanically vent the radon to the outside, so that radon levels are controlled within the building.

- If the system is activated, it must be capable of reducing and maintaining the radon concentration to as low as practicable below 200 Becquerels per cubic metre (Bq/m3) within the building, as per Health Canada guidelines.

1.2	REFERENCES

.1	Alberta Building Code 2014.

.2	EPA/625/R-92/016 - 1994 Radon Prevention in the Design and Construction of Schools and Other Large Buildings.

.3	ASTM applicable standards.

.4	Health Canada – Guide for Radon Measurements in Public Buildings – 2016.

.5	Health Canada – Guide for Radon Measurements in Residential Dwellings – 2017.

1.3	ADMINISTRATIVE REQUIREMENTS

.1	Pre-Installation Meeting:

- Contractor to arrange for a site meeting with the (C-NRPP) Certified Mitigation Professional to review existing conditions and all requirements related to materials, material handling and storage, installation, scheduling, testing, and quality assurance and control, to confirm compliance with manufacturer and installation requirements.

.2	Submittals:

- Submit component product information to the (C-NRPP) Certified Mitigation Professional related to the system design drawings and specifications. This includes the geotextile fabric, gas permeable venting layer, membrane barrier system, suction pit and cage, collection/extension/riser piping, and sealing methods for the slab perimeters and penetrations.

- Provide final as-building drawings to the (C-NRPP) Certified Mitigation Professional that indicate the final locations of the collection/extension/riser pipes and the suction pits and cages.

.3	Quality Control:

- Component installation for the radon mitigation rough-in system is to be done by competent and skilled workers having a minimum of three (3) years’ experience installing vapour barriers, sealants and waterproofing membranes.

- Installation workers are also to obtain appropriate training on radon mitigation systems from the (C-NRPP) Certified Mitigation Professional and the component product manufacturers.

- (C-NRPP) Certified Mitigation Professional to have on-going meetings with the Contractor to discuss and confirm compliances with the system design drawings and specifications.

1.4	DELIVERY, HANDLING AND STORAGE

- Ensure all products delivered to the site meet manufacturer’s quality requirements. Remove and do not use any defective products. Store and handle materials as per manufacturer’s requirements, recommendations and safety data sheets. Protect materials from construction and weather related damage using appropriate coverings and adequate ventilation.

1.5	ENVIRONMENTAL / SITE CONDITIONS

- All products and materials are to be stored at temperatures and environmental conditions that conform to manufacturer guidelines.

- Perform installation work only when the weather conditions are within installation guidelines established by manufacturer.

- Do not proceed with membrane barrier system installation until confirmation by the (C-NRPP) Certified Mitigation Professional that the substrate preparation and condition is suitable.

- Do not proceed with the concrete slab pour until confirmation by the (C-NRPP) Certified Mitigation Professional that the membrane barrier system preparation and condition is suitable.

1.6	System Design Alternatives

- A (C-NRPP) Certified Mitigation Professional may propose using alternative void space technologies in the system design other than venting layer (radon rock) and suction pit cage as identified in this technical specification.

- The alternative design system should provide a clear description of the proposed void space technologies necessary to determine compliance and demonstrate equivalent performance to venting layer (radon rock) and suction pit cage design.

- Proposed alternative void space systems, designed to meet the “Technical Design Requirements for Alberta Infrastructure Facilities, February 2018”, will be given consideration and may be accepted by the Province.

1.7	WARRANTY

- Provide a two (2) year warranty against slab perimeter and penetration sealing defects and/or deficiencies, and confirm that the materials meet performance specifications and installation requirements.

- Review all manufacturers’ requirements for warranty period before the commencement of work. Ensure that all materials and installations are in conformance with manufacturer and warranty requirements, system design, and requirements of this specification.

- All slab perimeter and penetration sealing defects and/or deficiencies that occur within the warranty period are to be corrected promptly by the Contractor at no expense to the Building Owner and the Province.

1.8	PERFORMANCE REQUIREMENTS

- Installation of the geotextile fabric, gas permeable layer, suction pits and cages, collection/extension/riser pipes, membrane barrier system, and sealing methods for the slab perimeters and penetrations for the building concrete in contact with the soil, is to comply with manufacturers requirements, system design, and the requirements of this specification.

- All system components are to be chemically compatible with the soil environment (ASTM E154-88).

- The radon  rock (gas permeable venting layer) is to be a minimum 100 mm layer of clean, coarse, aggregate meeting Size #5 specifications as defined in ASTM C33 / C33M - 16 Standard Specification for Concrete Aggregates, and as stated in the EPA/625/R-92/016 - 1994 Radon Prevention in the Design and Construction of Schools and Other Large Buildings document.

- The radon membrane barrier system (also is the vapour barrier) is to be a minimum, 10 mil polyolefin based resin sheet membrane, meeting the requirements of ASTM E 1745-11. Other membrane barrier systems may be proposed by the (C-NRPP) Certified Mitigation Professional in the system design.

- Radon membrane barrier system is to be overlapped and sealed at all perimeters and floor slab penetrations to provide a continuous seal of the building area in contact with the soil, as per manufacturer requirements, system design, and the requirements of this specification.

- Install and seal floor drains, suction pits/cages and collection/extension/riser pipes in accordance with EPA/625/R-92/016 - 1994 Radon Prevention in the Design and Construction of Schools and Other Large Buildings.

1.9	C-NRPP INSPECTION REQUIREMENTS

- Four (4) inspections of the system components and rough-in installations will be performed by a (C-NRPP) Certified Mitigation Professional. The results of these activities will be photographed and documented in written inspection reports prepared by the Professional and provided to the Building Owner and Province.

- The inspections are as follows:

.1	The (C-NRPP) Certified Mitigation Professional will inspect and document all relevant materials and products brought to the site for the purposes of radon mitigation rough-in system (1st inspection).

.2	The (C-NRPP) Certified Mitigation Professional will inspect, document and approve the completed installation of collection/extension/riser pipes, suction pits and cages and gas permeable venting layer, prior to the membrane barrier installation (2nd inspection).

.3	The (C-NRPP) Certified Mitigation Professional will inspect, document and approve the integrity of the membrane barrier system. They are also to conduct leak testing of the membrane barrier system after completed installation, prior to the concrete slab pour over the membrane to seal it (3rd inspection and testing).

.4	The (C-NRPP) Certified Mitigation Professional will inspect, document and approve the completed installation of slab perimeter and penetration sealing and capping and labeling of the riser pipes, once the concrete slab pour is completed (4th inspection).

2	Products

  - MANUFACTURER

- All products shall conform to the applicable ASTM standards and the EPA/625/R-92/016 - 1994 technical design document, and as indicated in the design drawings and specifications. Materials and components included for use are to be approved by the (C-NRPP) Certified Mitigation Professional.

2.2	GEOTEXTILE FABRIC

- The geotextile fabric is to be installed on the subsoil below the radon  rock gas permeable venting layer. The geotextile fabric protects the gas-venting layer from being contaminated with fines from the subsoil. Other geotextile fabric layers can be proposed by the (C-NRPP) Certified Mitigation Professional in the system design.

- The geotextile fabric is to have the following physical characteristics:

.1	Non-woven fiber construction with an apparent opening size of 0.15mm.

.2	Unit weight of 340 g/m2 (ASTM D5261)

.3	Grab tensile strength of 1100 N (ASTM D4632).

.4	Elongation of from 45 to 105% (ASTM D4632).

.5	Trapezoid tear resistance of 450N (ASTM D4533).

.6	Puncture resistance of 700N (ASTM D4833).

.7	Mullen Burst of 3600Pa (ASTM D3786).

2.3	GAS PERMEABLE VENTING LAYER

- The gas permeable venting layer (radon rock) is to be a minimum 100 mm layer of clean, coarse, aggregate meeting Size #5 specifications as defined in ASTM C33 / C33M - 16 Standard Specification for Concrete Aggregates, and as stated in the EPA/625/R-92/016 - 1994 Radon Prevention in the Design and Construction of Schools and Other Large Buildings document.

2.4	MEMBRANE BARRIER SYSTEM

- The radon membrane barrier system (also the vapour barrier) is to be a minimum, 10 mil polyolefin based resin sheet membrane, meeting the requirements of ASTM E 1745-11. Other membrane barrier systems may be proposed by the (C-NRPP) Certified Mitigation Professional in the system design.

- All membrane seams are to be prepared, overlapped and sealed as per the manufacturer’s recommendations.

- Supply and install an air/vapour barrier membrane (self-adhering type) of minimum 2mm thick, or an approved alternative by the (C-NRPP) Certified Mitigation Professional, as a transition between the radon membrane and upturn onto grade beams, foundation walls, footings or any item that penetrates the finished floor slab. Joints are to be designed to accommodate anticipated movement.

- The membrane is to be terminated with an upturn at the perimeter grade beams, foundation walls, footings and strip footings, and terminate between the beam, wall or footing and finished floor slab. Membrane is to terminate midway through the floor slab and be sealed and secured using a Termination Bar, mechanically fastened to the beam or footing on 300mm centers. Sealant to be applied to junction between membrane to footing, wall or beam, above Termination Bar.

- Gas tight seals are to be provided around the surfaces of all vertical penetrations. Such surfaces are to be prepared as per manufacturer’s requirements to facilitate membrane adherence. Use an air/vapour barrier membrane (self-adhering type) of minimum 2mm thick, sealants and construction tape as required providing a continuous seal between radon membrane and any pipe, conduit or other item that penetrates the floor slab.

- Once concrete floor slab has cured sufficiently to allow work to proceed on it, apply sealant to all penetration junctions on the top side of the finished floor slab.

2.5 	SUCTION PIT AND CAGE

- The suction pits and cages are to be designed by the (C-NRPP) Certified Mitigation Professional. This method exposes void areas in the gas permeable venting layer to facilitate depressurization, if required.

- The suction pit area is to be sized to fit a galvanized metal suction pit cage. The cages are used to prevent the gas permeable venting layer from entering the suction pits.

- Ensure that a vertical collection riser pipe extends from the suction pit and cage to 300 mm above the finished floor slab. Horizontal collection/extension pipes may be required in the system design.

2.6	COLLECTION, EXTENSION AND RISER PIPES

- The collection, extension and riser pipe locations are to be designed by the (C-NRPP) Certified Mitigation Professional, and shown on the design drawings. Collection pipes are to be placed into the clear granular material / gas permeable venting layer having a minimum, thickness of 100mm.

- The collection, extension and riser pipes are to consist of a minimum Schedule 40 non-perforated smooth walled 100mm (inside) diameter rigid pipe of PVC, High Density PE or ABS construction.

- The collection, extension and riser pipes are to be installed in accordance with the EPA/625/R-92/016 - 1994 Radon Prevention in the Design and Construction of Schools and Other Large Buildings document.

- A single vertical riser pipe is to be installed at each suction pit and cage location and extend from the suction pit and cage to a minimum of 300mm above the finished floor slab.

- The system design by the (C-NRPP) Certified Mitigation Professional may use collection piping or sleeves to draw radon gas from multiple sub-slab areas to a single suction pit, to minimize the number of suction pits. This would require holes to be created, as shown in the design, through the perimeter grade beams, foundation walls, footings and strip footings to allow piping to run through.

3	Execution

3.1	INSTALLATION

- Contractor to review footing, wall and grade beam building construction drawings, and review radon mitigation rough – in system design drawings and specifications to ensure proper understanding before installation. Discuss with the (C-NRPP) Certified Mitigation Professional as required.

- All installation work is to be inspected, tested and documented by the (C-NRPP) Certified Mitigation Professional.

- Each individual sub-slab area isolated by building footings, foundation walls or grade beams is to be connected to an installed radon roughed-in mitigation system. The system design may use collection piping to draw radon gas from multiple sub-slab areas to a single suction pit, to minimize the number of suction pits.

- The (C-NRPP) Certified Mitigation Professional will inspect and document all relevant materials and products brought to the site for the purposes of radon mitigation rough-in system (1st inspection).

- Prepare sub-grade surface prior to installation of the geotextile fabric, suction pits and cages, and collection, extension and riser piping, as per the elevations specified in the building construction drawings and radon mitigation rough – in system design drawings and specifications.

- Place geotextile fabric layer over the entire sub-grade surface, with sufficient overlaps as per the manufacturer’s requirements.

- Construct and install the suction pits and cages as close to the center of the sub-slab area as practicable, as per the radon mitigation rough – in system design drawings and specifications and manufacturer’s requirements.

- Install collection/extension/riser pipes in locations as per the radon mitigation rough – in system design drawings.

- The collection pipes are to be placed within the gas permeable venting layer.

- All pipe joints are to be solvent welded and fully inserted into coupling or fitting to ensure joint integrity as per manufacturer’s instructions.

- If the riser pipe penetrations through the floor slab cannot be installed in the center of the sub-slab area, an extension pipe must be installed so that it extends from the center of the suction pit and cage to the preferred pipe slab penetration location.

- Riser pipe floor slab penetrations are not to interfere with planned future use of the interior space. Confirm riser pipe penetration locations with the C-NRPP Mitigation Professional on site prior to installation.

- The space around the riser pipe installations must be considered for possible future pipe extensions. Future exterior exhaust locations are to be located a minimum of 2.0 meters from any opening in the building or adjacent building.

- Riser pipe installations are to ensure the same sized exhaust pipe extensions can be made to the exterior of the building through the wall or roof system, if required in the future.

- The gas permeable venting layer (radon rock) is to be a minimum 100 mm layer of clean, coarse, aggregate meeting Size #5 specifications as defined in ASTM C33 / C33M - 16 Standard Specification for Concrete Aggregates, and as stated in the EPA/625/R-92/016 - 1994 Radon Prevention in the Design and Construction of Schools and Other Large Buildings document.

- The gas permeable venting layer (radon rock) is to be constructed by placing, grading and compacting (if required structurally) it over the entire sub-grade surface, geotextile layer and collection/extension/riser piping. Ensure the suction pit and cage area remains clear of the gas permeable venting layer (radon rock).

- At completion of the substrate, component and gas permeable venting layer, the Contractor is to contact the (C-NRPP) Certified Mitigation Professional to inspect the installation of this portion of the system prior to the membrane barrier installation (2nd inspection). Results are to be documented by the (C-NRPP) Certified Mitigation Professional.

- When acceptance of the substrate, component and gas permeable venting layer installation has been provided by the (C-NRPP) Certified Mitigation Professional, the membrane barrier system construction can commence.

- Membrane barrier system is to be placed over the gas permeable venting layer (radon rock). All membrane overlaps and sealing is to be done as per the manufacturer’s requirements and specifications.

- Membrane barrier system installation is to be performed by trained qualified installers using manufacturer’s recommended techniques and equipment.

- Membrane barrier system is to be a minimum, 10 mil polyolefin based resin sheet membrane, meeting the requirements of ASTM E 1745-11.

- Membrane barrier system is to be installed and sealed around all vertical penetrations with sufficient overlap and using an air/vapour barrier membrane (self-adhering type) of minimum 2mm thick, sealant and construction tape or chemical welded seams as per manufacturer’s requirements and specifications.

- At completion of the membrane barrier system, Contractor is to contact the (C-NRPP) Certified Mitigation Professional to inspect the integrity of the membrane barrier system and conduct depressurization testing of the system (3rd inspection). Results are to be documented by the (C-NRPP) Certified Mitigation Professional.

- When acceptance of the radon mitigation rough – in system installation has been provided by the (C-NRPP) Certified Mitigation Professional, the floor slab construction can commence.

- Care must be taken not to puncture the membrane excessively during floor slab construction. To limit membrane puncture during floor slab construction, items such as rebar chair supports designed with a wide base (instead of legs) are to be used to better spread the rebar load.

- Once concrete floor slab has cured sufficiently to allow work to proceed on it, clean joint surfaces in accordance with manufacturer’s instructions and seal all finished floor slab perimeter cold joints and any other floor slab penetration junctions between dissimilar materials using high quality sealants suitable for use on each subject material surface. Test sealant to confirm adhesion with all surfaces prior to use. Joints are to be pre-designed to accommodate anticipated movement.

- The above slab exposed open top of the riser pipes must be capped and 100% solvent welded to provide a complete seal.

- The above slab exposed riser pipe and cap are both to be labeled to identify them as part of the “Radon Mitigation Rough-in System”.

- At completion of the slab perimeter and penetration sealing and capping and labeling of the exposed riser pipes, Contractor is to contact the (C-NRPP) Certified Mitigation Professional for a final inspection of the installation (4th inspection). Results are to be documented by a (C-NRPP) Certified Mitigation Professional.

- When acceptance of the installation of the slab perimeter and penetration sealing, capping, and labeling of the exposed riser pipes has been provided by the (C-NRPP) Certified Mitigation Professional, the passive radon mitigation rough-in system is considered complete.

- Deficiencies in the radon mitigation rough – in system are to be corrected in accordance with this specification and as per instructions from the (C-NRPP) Certified Mitigation Professional.

END OF SECTION