Section Cover Page

Section 33 10 10 2018-08-15 Water System

Use this Section to specify potable water piping between the water service source and the building distribution system.  This includes underground piping, valves, valve boxes, corporation service fittings, hydrants and other water system components.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Data Sheet:  General

.3	Specification Section Text:

1.	General

1.1	Intent

1.2	Related Sections

1.3	Reference Documents

1.4	Detail Drawings

1.5	Testing by Contractor

2.	Products

2.1	Pipe and Pipe Fittings

2.2	Valves and Valve Boxes

2.3	Corporation Service Fittings

2.4	Hydrants

2.5	Bedding Materials

3.	Execution

3.1	Bedding

3.2	Installation of Pipe and Pipe Fittings

3.3	Joint Connection Methods

3.4	Valve and Valve Box Installation

3.5	Hydrant Installation

3.6	Disinfection

.4	Detail Drawings:

33 10 10.01	Hydrant Installation

33 10 10.02	Valve Installation - Section

33 10 10.03	Valve Installation - Elevation

33 10 10.04	Water Riser & Curb Stop

33 10 10.05	Well Connection Detail

Selecting Steel Pipe Thickness(es):

Use following formula to determine required steel pipe thicknesses:

P = 2SE tm

D° - 2Ytm

where P = internal pressure in MPa

tm = minimum required wall thickness in mm

D° = outside diameter of the pipe in mm

SE = maximum allowable stress in the steel due to

internal pressure in MPa (use 46 MPa).

Y = a coefficient having values as follows:

For pipe with D°/tm ratio less than 6, value of Y is found from:

Y =   d

d + D°

where d = inside dia. in mm

For pipe with D°/tm ratio equal to or greater than 6, Y = 0.4

Note:  This formula does not take into account structural strength required to resist external forces which may become an important factor in deep bury installations.

The main cannot be put into service until it has passed the bacteriological test as set out by the local municipality.

END OF DATA SHEETS

1.	General

1.1	INTENT

.1	Read this Section in conjunction with Section 33 05 10 - Piped Utility Systems General Requirements.

1.2	RELATED SECTIONS

.1	Soil for Earthwork:	Section 31 05 13.

.2	Trench Excavating and Backfilling:	Section 31 23 38.

1.3	Reference documents

.1	American Society for Testing and Materials (ASTM):

| .1 | ASTM B88M-16 | Standard Specification for Seamless Copper Water Tube (Metric). |
| --- | --- | --- |

.2	American Water Works Associaction (AWWA):

| .1 | C104/A21.4-16 | Cement Mortar Lining for Ductile Iron Pipe and Fittings. |
| --- | --- | --- |
| .2 | C110-12 | Ductile Iron and Gray Iron Fittings |
| .3 | C111/A21.11-17 | Rubber-Gasket Joints for Ductile Iron Pressure Pipe and Fittings. |
| .4 | C200-17 | Steel Water Pipe, 6 In. (150 mm) and Larger. |
| .5 | C203-15 | Coal Tar Protective Coatings and Linings for Steel Water Pipes. |
| .6 | C205-18 | Cement Mortar Protective Lining and Coating for Steel Water Pipe - 4 In. (100 mm) and Larger - Shop Applied. |
| .7 | C206 17 | Field Welding of Steel Water Pipe. |
| .8 | C207-13 | Steel Pipe Flanges for Waterworks Service, Sizes 4 In. Through 144 In. (100 mm Through 3,600 mm) |
| .9 | C208-17 | Dimensions for Fabricated Steel Water Pipe Fittings. |
| .10 | C500-09 | Metal-Seated Gate Valves for Water Supply Service. |
| .11 | C502-14 | Dry-Barrel Fire Hydrants. |
| .12 | C504-15 | Rubber Seated Butterfly Valves. |
| .13 | C604-17 | Installation of Buried Steel Water Pipe-4 In. (100 mm) and Larger. |
| .14 | C800-14 | Underground Service Line Valves and Fittings. |

.3	Canadian General Standards Board (CGSB):

| .1 | CGSB 41-GP-25M | Pipe, Polyethylene, for the Transport of Liquids. |
| --- | --- | --- |

.4	Canadian Standards Association (CSA):

| .1 | CSA B137-1-17 | Polyethylene (PE) Pipe, Tubing, and Fittings for Cold-water Pressure Services. |
| --- | --- | --- |
| .2 | CSA B137.3-17 | Rigid Polyvinylchloride (PVC) Pipe and Fittings for Pressure Applications. |

1.4	DETAIL DRAWINGS

.1	Following detail drawings are appended hereto and form part of this Section:

33 10 10.01	Hydrant Installation

33 10 10.02	Valve Installation

33 10 10.03	Water Curb Stop Connection

33 10 10.04	Water Riser & Curb Stop

33 10 10.05	Well Connection Detail

1.5	TESTING BY CONTRACTOR

SPEC NOTE:  Include this article only when required.  Delete for projects involving only a service connection.

.1	Arrange and pay for labour, equipment and materials required to perform specified hydrostatic and leakage tests.

.2	Notify the Province at least 24 h in advance of all proposed tests. Perform tests in the presence of the Province’s representative.

.3	Where any section of system is provided with concrete thrust blocks, do not conduct tests until at least 5 Days after placing concrete or 2 Days if high early strength concrete is used.

.4	Before testing, bed and cover pipe between joints to prevent movement or snaking of pipe line when test pressure is applied.

.5	Leave joints, fittings and valves exposed for visual inspection.

.6	Prevent water line from freezing.

.7	Strut and brace caps, bends, tees, and valves, to prevent movement when test pressure is applied.

.8	Ensure minimum disruption to existing water supply during testing.

.9	Test procedure for polyethylene pipe:

.1	Follow manufacturer's recommended procedures.

.2	Locate and repair defects.

.10	Test procedure [for pipe other than polyethylene]:

.1	Open valves.  Expel air from main by slowly filling with potable water.

.2	[Fill cement-mortar lined pipe at least 24 h before testing to allow water absorption by pipe material.]

.3	Thoroughly examine exposed parts and correct for leakage as necessary.

.4	Apply hydrostatic test pressure of 50% greater than operating pressure or 750 kPa whichever is greater, based on elevation of lowest point in system and corrected to elevation of test gauge, for a period of 1 h.

.5	Examine exposed pipe, joints, fittings, and appurtenances while system is under pressure.

.6	Measure amount of water required to maintain test pressure for 1 h.

.7	For pipe with rubber gasket joints, leakage shall not exceed that determined by the following formula:

L = (ND) (SQUARE ROOT OF P)

70,500

where   L = allowable leakage in litres per hour.

N = number of joints in length tested.

D = nominal diameter of pipe in millimetres.

P = average test pressure kilopascals.

.8	For pipe with other than rubber gasket joints, leakage shall be 0 L/h.

.9	Locate and repair defects if leakage is greater than amount specified.

.10	Repeat test until leakage is within amount specified.

2.	Products

2.1	PIPE AND PIPE FITTINGS

.1	General:  Provide factory-fabricated pipe and pipe fittings of sizes, types, pressure ratings, and joining methods indicated.  Where not indicated, provide proper compatible products as required to provide a functional system.

.2	Steel Pipe and Pipe Fittings:

.1	Pipe:  to ANSI/AWWA C200-91.

.2	Fittings:  to ANSI/AWWA C208-83.

.3	Internal Lining:  cement-mortar, to ANSI/AWWA C205-95.

.4	External Coating:  [coal tar, to ANSI/AWWA C203-91] [polyethylene jacket].

.3	Polyvinyl Chloride (PVC) Pipe and Fittings:

.1	Pipe:  to CSA B137.3-93, [CI DR 18] [CI DR 25] [CI DR 14].

SPEC NOTE:  Normally specify CI DR 18.

.2	Fittings:  to CSA B137.3-93.

.3	Joints:  gasketed bell end, to CSA B137.3-93.

.4	Polyethylene (PE) Pipe and Fittings:

.1	Pipe Sizes Up To And Including NPS 6:  to CSA B137.1-M95, series [   ].

.2	Pipe Sizes Over NPS 6:  to CGSB 41-GP-25M, series [   ].

.3	Fittings:  Cast iron, to ANSI/AWWA C110/A21.10-93 [, internally lined with cement mortar, to ANSI/AWWA C104/A21.4-95].

.4	Joints:  Butt welded and/or mechanical.

.5	Copper Pipe:  to ASTM B88-M96.

2.2	VALVES AND VALVE BOXES

.1	Gate Valves:  to ANSI/AWWA C500-93, non-rising stem, square body, to open counter-clockwise.

.2	Butterfly Valves:  to ANSI/AWWA C504-94, [handwheel] [gear] operated.

.3	Valve Boxes:  cast iron, adjustable over a minimum of 450 mm complete with valve operating extension rod.

2.3	CORPORATION SERVICE FITTINGS

.1	Corporation Main Stops, Curb Stops and Curb Boxes:  to ANSI/AWWA C800-89.

.2	Curb Stop:  [     ] mm, brass, control rod, adjustable valve box [and curb-cock] key.  Assembly equipped with copper thaw line consisting of stranded 10 mm copper wire.

2.4	HYDRANTS

.1	Hydrants:  to ANSI/AWWA C502-94, compression type, complying with requirements of local authority having jurisdiction.

.2	Accessories:  chain for nozzle, tap and plug drain hole.

2.5	BEDDING MATERIALS

.1	Granular Material:  [Sand] [[    ] mm Crushed Gravel] as specified in Section 31 05 13.

3.	Execution

  - bedding

.1	Provide Class [A] [B] [C] bedding as indicated on detail drawing appended to Section 33 05 10.

3.2	INSTALLATION OF PIPE AND PIPE FITTINGS

.1	Steel Pipe:  Install to ANSI/AWWA M11-1991.

.2	PVC Pipe:  Install in accordance with manufacturer's installation instructions.

.3	PE Pipe:  Install in accordance with manufacturer's installation instructions.

3.3	JOINT CONNECTION METHODS

.1	Steel to Steel:

.1	Welded:  to ANSI/AWWA C206-91.

.2	Steel Flanges:  to ANSI/AWWA C207-94.

.3	[                          ].

.2	PVC to PVC:

.1	Gasketed Bell-End Joints:  to CSA B137.3-93.

.2	Solvent Cemented Joints:  to CSA B137.3-93.

.3	PVC to Cast Iron Fittings:

.1	Rubber Gasket Joints:  to ANSI/AWWA C111/A21.11-95.

.4	PE to PE:

.1	Thermal Butt Fusion Welded Joints:  in accordance with manufacturer's recommendations.

.5	PE to Cast Iron Fittings:

.1	Flanged Joints:  in accordance with manufacturer's recommendations.

3.4	VALVE AND VALVE BOX INSTALLATION

.1	Install as indicated on detail drawings.

.2	Centre and plumb valve box over valve.  Set box cover flush with finish grade.

.3	Install so that valve box does not transmit shock or stress to valve.

3.5	HYDRANT INSTALLATION

.1	Locate and set hydrants plumb.  Locate pumper nozzle perpendicular to the roadway with easy and immediate access.

.2	Set hydrants to grade, with nozzles 500 mm above ground minimum.

.3	Locate control valve 900 mm from hydrant.

.4	Install drainage pit 900 mm square by 600 mm deep filled with 50 mm washed gravel.  Encase elbow of hydrant in gravel to 150 mm above drain opening.  Do not connect drain opening to sewer.

.5	Brace barrels of hydrants against unexcavated earth using concrete backing.  Assure that drain openings remain free.

.6	In areas where water table reaches drain opening, plug opening to prevent infiltration of ground water.

3.6	DISINFECTION

.1	Disinfect water line by maintaining a minimum concentration of 50 mg/L of available chlorine throughout system for a period of 24 h.

.2	After the retention period, flush out line until chlorine concentration in water leaving main is not greater than 1 mg/L.

END OF SECTION