Section Cover Page

Section 33 50 10 2008-06-02 Gas Distribution System

Use this Section to specify requirements for Gas Distribution Systems installed by Alberta Infrastructure and not by Utility Company.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Data Sheet - General

.3	Specification Section Text:

1.	General

1.1	Intent

1.2	Related Sections

1.3	Section Includes

1.4	Unit Prices

1.5	Testing by Contractor

2.	Products

2.1	Materials Schedule

2.2	Steel Propane Tanks

2.3	Pipe Sleeves

3.	Execution

3.1	Pipe Laying, Generally

3.2	Laying Steel Pipe

3.3	Laying Polyethylene Pipe

3.4	Valves and Valve Box Installation

3.5	Building Regulator Installation

3.6	Propane Tank Installation

Applicable Standards:

.1	CAN/CGA-B149.1-M91	Natural Gas Installation Code

.2	CAN/CGA-B149.2-M91	Propane Installation Code

.3	CGA 3.16-M88	Lever Operated Non-Lubricated Gas Shut-off Valves

.4	CSA B51-95	Boiler, Pressure Vessel, and Pressure Piping Code

.5	CAN/CSA B137.4-92	Polyethylene Piping Systems for Gas Services

.6	CSA Z245.1-95	Steel Line Pipe

.7	CSA Z662-96	Oil and Gas Pipeline Systems

Consult CAN/CGA-B149.1-M91 and CAN/CGA-B149.2-M91 for system design information and guidelines on selection of materials.

For steel pipe use Schedule 40 if operating pressure is less than 860 kPa or if joints are welded or welded and flanged.  Use Schedule 80 if operating pressures are greater than 860 kPa or joints are threaded.

For above ground application, use Schedule 80 pipe.

Threaded joints are not allowed underground unless approved by Alberta Human Resources and Employment, Plumbing and Gas Safety Services Branch.

Coating for steel pipe:

.1  High Density Polyethylene

.2  Colour - Yellow

.3  Thickness (microns)	Pipe Size (mm)

686	  up to 25

762	     32

787	     38

863	  65 and 80

Polyethylene Pipe (PE):  Use Series 160 for road crossings, etc.  Otherwise use Series 125.  Threading and gluing for PE pipe is not permitted.

END OF DATA SHEETS

1	General

1.1	INTENT

.1	Read this Section in conjunction with Section 33 05 10 - Piped Utility Systems General Requirements.

1.2	RELATED SECTIONS

.1	Fill Materials:	Section 31 05 13.

.2	Trench Excavating and Backfilling:	Section 31 23 88.

1.3	SECTION INCLUDES

.1	This Section includes requirements for a gas distribution system, including materials, installation of pipes, appurtenances and testing of the completed system.

1.4	UNIT PRICES

SPEC NOTE:  Include this article for Unit Price Contracts only.

| Unit of Work Description | Unit of Measurement | Method of Measurement |
| --- | --- | --- |
| Gas pipe [and fittings] | m | Length installed, measured through valves and fittings |
| Valves, risers, building regulator | Each | Number installed |
| Propane tank and [concrete base] [regulator] [valves] [vaporizer controls] [tank piping] | Each | Number installed |

1.5	TESTING BY CONTRACTOR

.1	Test Medium:  Air, gas or inert gas such as carbon dioxide or nitrogen.

.2	Fill piping with test medium for 24 hours prior to actual test.

.3	For steel piping, subject pipe to pressure of 700 kPa for 24 hours.

.4	For polyethylene piping, subject pipe to pressure of 350 kPa or 1.5 maximum operating pressure whichever is greater, for 24 hours.

.5	Supply pumps, connections, gauges, test medium, and other necessary apparatus required for test.

.6	Test shall consist of visual "soap bubble" inspection of the joints for leaks and of measuring the pressure after 24 hours.  No pipe installation will be accepted if leaks are detected or if pressure at end of test is less than 95% of original test pressure.

.7	If air or inert gas is used for testing, purge lines with natural gas before using.

2.	Products

2.1	MATERIALS SCHEDULE

| Material | Standard | Type | Joints | Sizes |
| --- | --- | --- | --- | --- |
| Steel pipe | CSA Z245.1-95 | Schedule [40] [ 80 ] | [Welded] [Flanged] [Threaded] | [ ] |
| Polyethylene pipe (PE) | CAN/CSA B137.4-92 | Grade 3406 Series [125] [ 160 ] | [Butt Fusion] [Socket Fittings] [Compression] | [ ] |
| Plug gas valves [c/w cast iron curb box, cover and key] | CGA 3.16-M88 | [Steel] [Grey Iron] | [ ] | [ ] |
| Pressure lubricated plug gas valves [c/w cast iron curb box, cover and key] | CGA 3.16-M88 | Steel | [ ] | [ ] |
| Plug valve (900 kPa working pressure) [c/w cast iron curb box, cover and key] | CGA 3.16-M88 | Bronze | [ ] | [ ] |
| Building regulator | Inlet pressure 860 kPa Outlet pressure 20 kPa to 3.7 kPa | Malleable Iron Body, Fisher Model S102 |  | [20mm] [25mm] |

SPEC NOTE:  Use only steel valves with steel lines and bronze valves with copper lines.  For PE lines, either steel or bronze valves can be used.  Use pressure lubricated plug valve for operating pressure above 415 kPa.

2.2	STEEL PROPANE TANKS

.1	Conform to CSA B51-95.

.2	[1900] [3800] [7600] L cylindrical steel tank with hemispherical ends, 1025 mm diameter, minimum design pressure of 1700 kPa, and approved by authority having jurisdiction.

.3	Tank shall be of new stock.  Paint with one coat of red primer paint and two coats of silver anti-rust paint.

.4	Concrete Tank Supports:  to CAN/CGA-B149.2-M91.

.5	Tank Heater (vaporizer):  1000 W, 115 V heating cable bedded in 25 mm of fiberglass insulation and covered with a flexible stainless steel plate.

.6	Thermostat control box:  (2P-20 A) set to turn on at -25 degrees Celsius complete with weatherproof box and on-off switch.

2.3	PIPE SLEEVES

.1	Steel Pipe to CSA Z662-96.

3.	Execution

3.1	PIPE LAYING, GENERALLY

.1	Provide recesses on trench bottom for couplings, fittings and valves to ensure bearing will occur along barrel of pipe.

.2	In roads, streets, driveways, and parking areas, provide steel pipe sleeve of diameter 50 mm greater than gas pipe diameter.  Install gas pipe in pipe sleeve in accordance with CSA Z662-96.

.3	Lay service line pipe on proper grade to drain from building to gas main.

.4	Lay gas pipe on properly graded trench bottom to prevent sags and low points in piping.

.5	Ensure minimum of 1000 mm between gas pipe and any underground structure that runs parallel to gas pipe.

.6	Ensure minimum of 100 mm between gas pipe and any underground structure that crosses gas pipe.

3.2	LAYING STEEL PIPE

.1	Lay pipe on 50 mm cushion of compacted clay fill or on flat, undisturbed trench bottom.  Backfill excavated material thoroughly tamped in place.

.2	Lower pipe carefully into trench to prevent damage to coating.

.3	Wrap couplings and fittings with polyethylene tape and heat shrink over pipe.

3.3	LAYING POLYETHYLENE PIPE

.1	Lay pipe on undisturbed trench bottom.  Backfill around sides and to top of pipe with [native excavated material] [sand] thoroughly tamped in place.

.2	Install tracer wire securely fastened to pipe, and brought to ground surface at locations shown and as detailed on [drawing No.    ].

3.4	VALVE AND VALVE BOX INSTALLATION

.1	Locate valves as shown on drawings.

.2	Set valves on solid bearing.

.3	Centre and plumb valve box over valve.  Set box cover flush with finished ground surface.  Prevent shock or stress from being transmitted through valve box to valve.

.4	For steel valves and cast iron valve boxes, wrap valve and valve box with polyethylene tape and heat shrink, or paint valves and valve boxes with red anti-rust primer and one coat of epoxy paint.

3.5	BUILDING REGULATOR INSTALLATION

SPEC NOTE:  Include this article only when contractor is to supply regulator eg. propane tank systems.  Natural gas companies usually supply and install the regulator as part of the service connection.

.1	Install service regulator adjacent to building wall as shown on drawing No. [              ].

.2	Install service regulator and riser pipe in such manner as to prevent undue stress upon service pipe.  For plastic service pipe, use steel pipe riser from below ground to regulator.

.3	Ensure regulator vent has rain and insect proof opening and terminates away from building openings.

3.6	PROPANE TANK INSTALLATION

.1	Locate propane tank horizontally to alignment specified to within tolerance of 300 mm.

.2	When two or more tanks are attached to a common supply manifold, ensure tops of all tanks are at same elevation.

.3	Prepare area of 2.0 m all around tank by grading level, compacting subgrade, and placing 25 mm crushed gravel to compacted depth of 75 mm.

.4	Place tank on concrete tank supports and ensure tank is level to within tolerance of [50] [75] mm.  Provide concrete tank supports for each end of propane tank.

.5	Provide each propane tank with relief valve, shut-off valve, pressure regulator, pressure gauge and removable protection cover.  Set tank regulator to have outlet pressure of [70] [100] [140] kPa.

.6	Install necessary propane tank piping, shut-off valve and pressure gauge to connect to underground piping.

.7	Install tank heater (vaporizer) to underside of each tank and secure to tank with aluminum tray and two stainless steel straps.

.8	Install weatherproof control box for vaporizer 1,000 mm above ground surface on 89 mm x 89 mm pressure treated cedar post, driven into ground 1,000 mm.

.9	Install wiring from vaporizer to control box 500 mm below ground surface.  Wiring size to be as shown on drawings.

.10	Install service wiring 600 mm below ground from control box to building panel as shown on drawings.

END OF SECTION