Section Cover Page

Section 10270 2000-04-20 Access Flooring

Use this section to specify "elevated" or "raised" access flooring systems.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Data Sheet – General

.3	Specification Section Text:

1.	General

1.1	Related Work Specified In Other Sections

1.2	Product Options and Substitutions

1.3	Description of System

1.4	Installer Qualifications

1.5	Performance and Design Requirements

1.6	Mock-up

1.7	Source of Supply

1.8	Samples

1.9	Shop Drawings

1.10	Certificates

  - Maintenance Data

  - Maintenance Materials

2.	Products

2.1	Product Manufacturers

2.2	Pedestals

2.3	Steel Floor Panels

2.4	Composite Steel Floor Panels

2.5	Aluminum Floor Panels

2.6	Stringers

2.7	Vinyl Seal

2.8	Ramps [and Steps]

2.9	Fascia Panels

2.10	Railings and Posts

2.11	Base

2.12	Accessories

2.13	Metal Finishes

  - Flooring Finishes

3.	Installation

3.1	General

3.2	Pedestals and Stringers

3.3	Floor Panels

3.4	Fascia Panels

3.5	Railings

3.6	Plenum Dividers

3.7	Base

3.8	Grounding

3.9	Protection of Finished Work

3.10	Schedule

Applicable Standards

.1	CAN3-A172-M79(R1996)	High Pressure Paper Base, Decorative Laminates

.2	CAN/CGSB-4.129-93	Carpet for Commercial Use

.3	CAN/CGSB-51.33-M89	Vapour Barrier Sheet, Excluding Polyethylene, for Use in Building Construction

These reference documents may be available for reference purposes in the Technical Resources and Standards Branch Library, Alberta Infrastructure, 3rd Floor, 6950 - 113 Street, Edmonton; Telephone: (780) 427-7924.

Verify design requirements to include for:

.1	Stairs, ramps and railings.

.2	Excessive floor loading.

.3	Cable cutouts.

.4	When flooring system must be sealed as a plenum, check for plenum dividers and zoning divisions.  Verify and coordinate plenum requirements with mechanical sections.

When the underfloor cavity is an air distribution plenum for electronic data processing equipment, ensure that potential sources of dust such as unsealed concrete are eliminated to the extent possible.

Floor coverings and bases are available in a wide range of materials and applications.  Refer to applicable sections of Division 9 for detailed specifications for materials to be included in this section.

1.	General

1.1	RELATED WORK SPECIFIED IN OTHER SECTIONS

.1	Ventilation and related mechanical work:	Division 15.

.2	Grounding and related electrical work:	Division 16.

1.2	PRODUCT OPTIONS AND SUBSTITUTIONS

.1	Refer to Division 1 for requirements pertaining to product options and substitutions.

1.3	DESCRIPTION OF SYSTEM

.1	General Description:  Raised, adjustable access flooring system consisting of support system, interchangeable flooring panels, finished flooring, bases associated components and accessories.

.2	Dimensions:

.1	Horizontal Module:  [           ].

.2	Height:  [    ] mm to [    ] mm.

.3	Vertical Adjustability:  [     ] mm.

.3	Support System:

.1	Pedestals

.2	Removable stringer grid, [unexposed] [exposed].

[OR]

.2	Fixed stringer grid, [unexposed] [exposed].

[OR]

.2	Stringerless (no grid).

.4	Pedestals:

.1	Adjustable [Steel] [or] [Aluminum]

.5	Floor Panels - one of the following:

.1	Steel.

.2	Aluminum.

.3	Composite wood and metal.

.6	Floor Panel Finish:

.1	Carpet.

.2	Vinyl Asbestos Tile.

.3	Non-slip Rubber.

.4	Melamine phenolic laminate.

.5	Homogenous vinyl sheet.

.6	[                         ].

.7	Accessibility:

.1	All floor panels removable.

.2	Full size panels interchangeable.

.3	Panel lifting device to suit floor covering.

1.4	INSTALLER QUALIFICATIONS

.1	Installation of access floor shall be an applicator authorized by manufacturer of system being installed.

1.5	PERFORMANCE AND DESIGN REQUIREMENTS

.1	Evenness of Surface:

.1	Maximum variation 1:2000 over entire floor.

.2	Strength:

.1	Twice design strength minimum.

.2	Complete rigid assembly when eight abutting panels are removed.

.3	Pedestals:

.1	Maximum axial load:  [22] kN with no deflection.

.2	Ultimate load carrying capacity:  not less than twice design strength.

.4	Adhesive Strength:

.1	Minimum 178 N horizontal force applied to 300 mm high pedestal without bond impairment.

.5	Floor panels:

.1	Live load [12] kN/m2:  maximum deflection [1] mm.

.2	Concentrated load [7] kPa at any location:  maximum deflection [2] mm.

.3	Permanent deflection:  maximum [0.5] mm at design load.

.6	Allowable component tolerances:

.1	Floor panel flatness:  ± [0.5] mm in any direction.

.2	Floor panel surface dimension:  ± [0.5] mm.

.3	Floor panel squareness:  ± [0.5] mm in panel surface dimension and [0.25] mm measured diagonally.

.7	Surface electrical resistance not to exceed [2 x 1010] ohms nor be less than [5 x 105] ohms.

SPEC NOTE:  Verify surface electrical resistance requirements, of equipment to be installed.  Coordinate resistance values with floor finish.

1.6	MOCK-UP

.1	Site assemble an 1800 mm x 1800 mm of access flooring where directed.

.2	Obtain Minister's approval of mock-up before starting installation.

1.7	SOURCE OF SUPPLY

.1	All components of system shall be of single manufacturer/supplier [including] [excluding] floor finishes.

1.8	SAMPLES

.1	Comply with requirements of Division 1.

.2	Submit [duplicate] samples of:

.1	[200 x 300] mm of each floor covering type, colour, pattern and finish.

.2	[300] mm long cove base.

SPEC NOTE:  Verify project needs.  Delete 1.7 when finished flooring is specified in another specification section.

1.9	SHOP DRAWINGS

.1	Comply with requirements of Division 1.

.2	Indicate:

.1	Floor panel layout.

.2	Component details.

.3	Anchorage methods.

.4	Edging details.

.5	Elevation differences.

.6	Fascias, step, ramp and handrail details.

.7	Grilles, registers and perforated panels.

1.10	CERTIFICATES

.1	Submit certificates provided by an independent nationally recognized testing organization certify:

.1	Specified design strengths.

.2	Flame spread ratings.

.3	Electrical resistances.

1.11	MAINTENANCE DATA

.1	Comply with requirements of Division 1.

.2	Include data in Maintenance Manual for maintenance of:

.1	Floor finishes.

.2	Access flooring systems and components.

1.12	MAINTENANCE MATERIALS

.1	Provide [         ] spare floor panels.

.2	Provide [         ] spare pedestals, associated stringers and components.

.3	Provide [       ] panels of finished floor materials, of same production run as installed materials.

.4	Identify each carton of materials.

.5	Store where directed.

SPEC NOTE:  Check requirements for maintenance materials and storage availability with maintenance forces.  On larger projects, it is suggested 2%-5% of installed material area be allowed for maintenance purposes.  Include 1.11 only if Access Flooring supplier is providing finished flooring.

2.	Products

2.1	PRODUCT MANUFACTURERS

SPEC NOTE:  Include 2.1 only when the use of a proprietary specification is deemed essential.  Normally this article will not be required.

.1	Access Flooring System:  by one of the following:

.1	[Manufacturer's Name, Address, etc.], [Model no. etc.].

.2	[                                  ], [              ].

.3	[                                  ], [              ].

.4	[                                  ], [              ].

.2	Substitutions will not be accepted.

SPEC NOTE:  Specify 2.1.2 above only  when the named manufacturers meet project requirements.  This must be approved by Specifications and Standards Section.

2.2	PEDESTALS

.1	[Steel] or [Aluminum].

.2	Base Plates:  10,000 mm2.

.3	Threaded supporting rod, vibration proof locknut, 38 mm minimum adjustment.

.4	Manufacturer's standard [galvanized] finish.

.5	Adjustable from horizontal plane 4°, to compensate for uneven sub-floor.

2.3	STEEL FLOOR PANELS

.1	[          ] mm x [        ] mm.

.2	Die formed.

.3	Bottom Plate  reinforced steel welded to flat steel die cut top plate.

.4	Manufacturer's standard [Baked Enamel] finish.

2.4	COMPOSITE STEEL FLOOR PANELS

.1	[     ] mm x [    ] mm.

.2	[Particle board] or [plywood] core.

.3	Galvanized sheet steel skin bonded to all faces of core with thermosetting adhesive.

2.5	ALUMINUM FLOOR PANELS

.1	[     ] mm [     ] mm.

.2	Die cast:  rough spots and cast imperfections removed, edges machined.

SPEC NOTE:  Select panel construction from 2.3, 2.4 or 2.5 if required.

2.6	STRINGERS

.1	Continuous or removable type.

.2	[Steel] or [Aluminum].

.3	Shaped to receive integrally extruded vinyl seal on top surface.

2.7	VINYL SEAL

.1	Located on stringers or floor panels.

.2	Electrically conductive.

.3	Shaped to seal off air plenum under finished access floor panels.

2.8	RAMPS [AND STEPS]

.1	Same materials, structural strength and construction as floor panels.

.2	Cover open joints with flush [aluminum] or [stainless steel] cover plates.

2.9	FASCIA PANELS

.1	Construction and finishes to match floor panels.

.2	Include corner pieces, trim, reinforcing and fixing angles required.

2.10	RAILINGS AND POSTS

.1	[Extruded aluminum] or [galvanized steel].

.2	[Welded] [Sleeved] connections.

.3	Include cast metal end caps, floor sockets, collars, brackets and fittings required.

.4	[Anodized] [Baked enamel] manufacturer's standard finish.

2.11	BASE

.1	Extruded [vinyl] [rubber] with preformed corners.

.2	[63] [100] [150] mm high.

.3	Colour [indicated on finish schedule] [selected by Minister from manufacturer's standard range].

SPEC NOTE:  Delete base if specified to be supplied and installed in other flooring Sections.

2.12	ACCESSORIES

.1	Panel lifting device:

.1	[1] [2] per enclosed area.

.2	Type recommended for each panel type.

.3	Manufacturer's standard design.

.2	Perforated floor panels:

.1	Same size, materials and construction as floor panels. [with slide damper].

.2	[10] [   ]% free area.

.3	Air grilles:

.1	[    ] mm x [     ] mm.

.2	Live load design  [4.8] [    ] kN/m2.

.3	[Straight] [Deflecting] vanes.

.4	Shutoff damper.

.5	[Galvanized sheet steel with baked enamel finish] [anodized extruded aluminum].

.4	Grounding connectors:  solid copper.

.5	Adhesives:  [moisture resistant] [waterproof] [electrically conductive] type [as recommended by manufacturer].

.6	Cable cutout protection:

.1	[Extruded polyvinyl chloride] or [neoprene edging] or [closed cell neoprene sheet].

.2	[9.5] [     ] mm thick.

.3	Self-extinguishing and non-burning.

.7	Plenum divider:

.1	Galvanized sheet steel.

.2	0.46 mm thick to 330 mm high.

.3	0.6 mm thick above 300 mm high.

.8	Trim:  to match finish floor [and fascia panels] except where noted otherwise.

.9	Polyethylene sheet:  to CAN/CGSB-51.33-M89, Type 2.

2.13	METAL FINISHES

.1	Aluminum components:

.1	Provide mechanical, chemical and anodic finishes in accordance with Aluminum Association Designation System for Aluminum Finishes-1973.

.2	Steel components:

.1	Exposed steel components:

.1	Painted:  [Gloss] [Semi-gloss].

.2	Colour selected by Minister from manufacturer's standard range.

.2	Concealed steel components:  1 coat baked primer.

SPEC NOTE:  Delete concealed paint finish if not required.

2.14	FLOORING FINISHES

SPEC NOTE:  Determine if Access Flooring Manufacturer is to provide the chosen floor finishes.

.1	Factory applied [3] mm thick, vinyl asbestos tile.

.2	Factory applied [3] mm thick homogenous vinyl [tile] [sheet].

.3	Factory applied [3] mm thick, melamine phenolic laminate to CAN3-A172-M79 designed for floor panel use.

.4	Carpet:  [manufacturer's standard] [to CAN/CGSB-4.129-93].

SPEC NOTE:  Refer to 09680 for detailed specification.  When reference is made to CAN/CGSB 4.129-93 specify pile fibre, cushion backing, static control, medium or heavy traffic conditions. Consult with Access Flooring manufacturer.

.5	Factory applied [3] mm thick ribbed, non-slip rubber flooring.

SPEC NOTE:  Specify finish floor materials from list 2.14.1 to 2.14.4.  If more than one material is required for a project, specify locations.

.6	Finish panel edges with vinyl trim.

3.	Installation

3.1	GENERAL

.1	Install components to system manufacturer's instructions.

3.2	PEDESTALS AND STRINGERS

.1	To meet grid spacing required.

.2	Bond pedestals base plate to structural floor with adhesive.

.3	Install additional pedestal assemblies where required to maintain load capacity.

.4	Brace floor pedestals four ways with stringers.

3.3	FLOOR PANELS

.1	Install [grilles] [perforated panels] where indicated.

.2	Install [ramp] [and] [step tread] panels similar to floor panels, securely fixed.  [Include shoe at top and bottom of ramp].

.3	Seal field cuts with plastic angles or channels.  No exposed cut edges permitted.

.4	Install required edge trims, end closures.

.5	Allow for cutting [        ] hundred [       ] mm dia. holes in floor panels for installation of equipment [and air conditioning units].  Include cable protection edging or sheet.

3.4	FASCIA PANELS

.1	Install fascia panels at:

.1	Exposed sides.

.2	Ramp sides.

.3	Step risers.

.4	Where indicated.

.2	Secure panels to continuous clip angles.  Mechanically Secure to structural floor and to edge of floor panels.

.3	Install metal trim at intersection of fascia panels and access floor [and at abutting walls and columns].

3.5	RAILINGS

.1	Extend railing posts through floor panels.

.2	Secure to structural floor below with bolted flanged fittings.

.3	Bolt posts in position at floor panels with retaining floor collar.

.4	Set wall railings into flanged fittings bolted to walls.

.5	Electrically insulated or directly ground to access flooring system.

3.6	PLENUM DIVIDERS

.1	Install positive air seal between sub-floor and elevated floor.

.2	Install sponge rubber cut-out panels at wiring holes in plenum.

SPEC NOTE:  Ensure drawings indicate number and locations of plenum dividers.

3.7	BASE

.1	Bond base along intersection of walls and access floor panels.

SPEC NOTE:  Delete 3.7 when base is specified in Division 9.

3.8	GROUNDING

.1	Install electrical ground connectors.

3.9	PROTECTION OF FINISHED WORK

.1	Protect finished access floor with:

.1	Kraft paper.

.2	0.15 mm thick polyethylene film.

.3	Seal at edges to prevent tearing.

SPEC NOTE:  Specify polyethylene film for carpet finish.

3.10	SCHEDULE

|  | Floor Finish | Location |
| --- | --- | --- |
| .1 | Vinyl Asbestos Tile: | [ ] |
| .2 | Homogenous Vinyl: | [ ] |
| .3 | Melamine Laminate: | [ ] |
| .4 | Carpet - Type I: | [ ] |
|  | - Type II: | [ ] |
|  | - [ ]: | [ ] |
| .5 | Non-Slip Rubber: | [ ] |
| .6 | [ ]: | [ ] |

END OF SECTION