Section Cover Page

Section 13281 Asbestos Control 2007-03-26 General Requirements

Use this Section, as applicable, in conjunction with Section 13282 - Asbestos Containment Procedures, Section 13283 - Asbestos Removal, and Section 13284- Asbestos Encapsulation.

Edit this Section only in consultation with Alberta Infrastructure and Transportation specialists in asbestos control procedures.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Data Sheet - General

.3	Specification Section Text:

1.	General

1.1	Intent

1.2	Related Work Not Provided Under This Contract

1.3	Related Sections

1.4	Reference Documents

1.5	Definitions

  - Worker Qualifications

  - Submittals

1.8	Regulatory Requirements

1.9	Monitoring and Inspection By Minister

1.10	Testing and Air Monitoring by Contractor

1.11	Airborne Fibre Levels

1.12	Protection of Personnel

2.	Products

2.1	Material and Equipment

2.2	Asbestos Disposal Containers

2.3	Warning Signs

3.	Execution

3.1	Preparation

3.2	Asbestos [Removal] [Encapsulation]

3.3	Preparation For Asbestos Disposal

3.4	Disposal of Normal Construction Waste

3.5	Transportation and Permanent Disposal of Asbestos Waste

3.6	Worker Decontamination

3.7	Daily Cleaning

3.8	Final Cleaning

# CONTRACT PLANNING

There are two options available for contracting for asbestos control work in connection with Alberta Infrastructure and Transportation work:

Option 1:  Alberta Infrastructure and Transportation contracts for asbestos control work under a single contract with an asbestos control contractor.

Option 2:  Alberta Infrastructure and Transportation contracts for asbestos control work as a subcontract under a renovation contract.

Select the contracting option most appropriate for the project and edit this Section to suit the option selected.

## INDUSTRIAL WASTE CLASSIFICATION

Asbestos is classified as a waste dangerous good and must be transported in accordance with:

.1	Environmental Protection and Enhancement Act (Alberta)

.2	Transportation of Dangerous Goods Act, 1992 (Canada)

.3	Transportation of Dangerous Goods Control Act (Alberta) and regulations

The owner of the property (i.e., the Minister) is considered to be the waste generator.

1.	General

1.1	INTENT

.1	This Section specifies general requirements common to all asbestos control work.  Read this section in conjunction with related Sections that specify requirements for specific procedures and methods for asbestos control.

1.2	RELATED WORK NOT PROVIDED UNDER THIS CONTRACT

SPEC NOTE:  Coordinate this article with Division 1 requirements on user occupancy.

.1	Following related work will be performed by Minister's own forces or by user:

.1	Moving of removable furniture and equipment from asbestos control area before work begins.

.2	[                                    ].

  - RELATED SECTIONS

SPEC NOTE:  Retain only Sections applicable project.

.1	Asbestos Containment Procedures:	Section 13282.

.2	Asbestos Removal:	Section 13283.

.3	Asbestos Encapsulation:	Section 13284.

  - REFERENCE DOCUMENTS

.1	Asbestos Abatement Manual, Current Edition, available from:  Alberta Employment, Immigration and Industry, Information Services, 2nd Floor, Labour Building, 10808 – 99 Avenue, Edmonton, Alberta, T5K 0G5, Telephone:  (780) 427-8531.

.2	Guidelines for the Disposal of Asbestos Waste, available from Alberta Environmental Protection.

.3	CAN/CGSB-1.205-94, Sealer for Application to Asbestos-Fibre Releasing Materials.

.4	CAN/CGSB-43.150-97, Performance Packagings for Transportation of Dangerous Goods.

1.5	DEFINITIONS

.1	Asbestos Control Work:  means asbestos containment procedures, removal or encapsulation, and disposal of asbestos or materials containing asbestos, as specified.

.2	Asbestos Control Area:  means space in which asbestos control work is being performed and to which general access is prohibited.

.3	Asbestos Waste:  means removed contaminant and contaminated materials or products.

.4	Contaminant:  means asbestos material.

.5	Contaminated:  describes products, by-products, or material containing, or affected by, asbestos or removal thereof.

.6	Full Containment Procedures:  means construction of temporary facilities and following of procedures to contain asbestos fibres, as specified in Section 13282.

.7	HEPA Filter:  high efficiency particulate air filter, removing not less than 99.97% of particles measuring 0.3 microns and larger, for powered respirators, vacuums, vacuum trucks and negative air units.

.8	P100 Filter:  high efficiency, oil proof, particulate air filter, removing not less than 99.97% of particles measuring 0.3 microns and larger, for non powered air purifying respirators.

1.6	WORKER QUALIFICATIONS

.1	Workers used for handling, removal, and packaging for disposal of asbestos waste, shall have completed an asbestos control course acceptable to Alberta Employment, Immigration and Industry, Workplace Health and Safety and be certified to remove asbestos.

.2	At least one employee who will be performing the work shall have completed a first aid course as required by Alberta Occupational Health and Safety Act.

.3	Persons involved in loading, transportation, uploading, and disposal of asbestos waste shall have been trained in accordance with the Dangerous Goods Transportation and Handling Act.

SPEC NOTE:  Contact Alberta Infrastructure and Transportation to determine if paragraphs 1.6.4, 1.6.5 or 1.6.6 are required.

.4	Workers shall attend an asbestos awareness session conducted by the Minister’s designated air testing consultant prior to the start of asbestos control work, to obtain:

.1	information describing the medical effects of asbestos exposure,

.2	information regarding the proper use of respirators and other personal protection equipment, and

.3	instructions as to the proper asbestos removal and disposal procedures for this project.

.5	Non-certified workers such as heavy equipment operators may be used for loading and transporting the asbestos containing debris to an approved sanitary landfill site.  These workers require dangerous goods training as specified in this Section.

.6	Workers are required to attend an asbestos awareness session conducted by the Minister’s designated air testing consultant prior to start of asbestos control work.  The purpose of this session is to educate workers about the medical effects of asbestos exposure, provide instructions on the proper use of respirators and other personal protection equipment and on proper asbestos removal and disposal procedures for this project.

1.7	SUBMITTALS

SPEC NOTE:  Edit paragraph 1.7.1 to suit project.

.1	Comply with requirements of [this Section and] Division 1.  Provide submittals prior to start of asbestos control work.

.2	Submit copy of test results documenting Dioctylpthalate (DOP) testing of HEPA filtered vacuums and negative air units.

.3	Submit certification that HEPA filtered vacuums required for this contract meet specified HEPA filter designation for component filter assemblies.

.4	Submit disposal procedure for contaminant and contaminated waste.

.5	Submit a copy of "Manual of Safe Practice" for the work, required by the Occupational Health and Safety Act.  Submit proof that Alberta Employment, Immigration and Industry, Workplace Health and Safety has reviewed the manual.

.6	Submit a copy of worker protection information which will be provided to employees.

.7	Submit plan for air monitoring to ensure use of proper respirators within work area.

.8	Submit proof that Alberta Employment, Immigration and Industry, Workplace Health and Safety, has been notified of the asbestos control work to be performed.

.9	Submit proof that all persons involved in the handling, packing, loading, transportation, unloading, and disposal of asbestos waste are trained in accordance with the Dangerous Goods Transportation and Handling Act.

SPEC NOTE:  Use following clause when asbestos control work is part of a larger renovation contract.  If asbestos control work is the primary element of the contract, delete this clause and specify all schedule requirements in Division 1.

.10	Provide sub-schedule for asbestos control work.

SPEC NOTE:  Include the following clause only if Section 13282, Asbestos Containment Procedures, is used.  If tender documents provide detailed documentation required under Asbestos Control Plan, edit submittal requirements accordingly.

.11	Prior to commencement of work on site, submit an Asbestos Control Plan.  Include the following information:

- Locations of:

.1	Asbestos control areas

.2	Change rooms

.3	Isolation/Containment barriers

.4	Decontamination facilities

.5	Negative air units

.6	Exhaust for negative air units

.2	Layout of change rooms.

.3	Sequencing of asbestos related work.

SPEC NOTE:  Include the following clause only if Section 13283, Asbestos Removal, is used.

.12	Prior to start of asbestos removal, submit product data for proposed surfactant.

SPEC NOTE:  Include the following clause only if Section 13284, Asbestos Encapsulation, is used.

.13	Submit product data for proposed encapsulating sealant.

1.8	REGULATORY REQUIREMENTS

.1	Comply with the following legislation and regulations:

.1	Environmental Protection Act (Canada).

.2	Environmental Protection and Enhancement Act (Alberta).

.3	Occupational Health and Safety Act (Alberta).

.4	Chemical Hazards Regulation (Alberta).

.5	Transportation of Dangerous Goods Act, 1992 (Canada).

.6	Dangerous Goods Transportation and Handling Act (Alberta) and regulations.

.7	Other legislation and regulations which apply to the performance of asbestos control work.

1.9	MONITORING AND INSPECTION BY MINISTER

.1	Minister will [appoint and pay for services of testing agency] [utilize the Minister’s own forces] to perform the following:

.1	Measure asbestos fibre levels inside and outside asbestos control area prior to commencement of asbestos control work.

.2	Inspect negative air units and HEPA vacuums prior to commencement of asbestos control work.

.3	Monitor air outside asbestos control area and where glovebag removal method is used.  Monitor air prior to, during, and after asbestos control work.

.4	Monitor asbestos fibre levels inside asbestos control area prior to removal of barriers.

.2	Testing agency engaged by Minister to perform air monitoring is authorized to identify deficiencies in the asbestos control work and provide site instructions to ensure compliance with Contract requirements.

.3	In the event that airborne asbestos fibres exceed acceptable level, Minister may stop work until corrective actions have been taken and airborne fibres return to acceptable level.

.4	Minister may stop work where he has reasonable cause to believe that:

.1	fibre levels inside asbestos control area are unacceptable, or

.2	work conditions and practice may lead to:

.1	contamination of building with asbestos,

.2	asbestos exposure to building occupants, or

.3	release of asbestos fibres into the environment.

1.10	TESTING AND AIR MONITORING BY CONTRACTOR

.1	Appoint and pay for services of a testing agency to perform Dioctylpthalate (DOP) testing on completed installation of negative air units and HEPA vacuums, in accordance with Medical Research Council of Canada, 1980 Guidelines and/or field applications of United States Military Standards Number 282 and U.S. Army Instruction Manual 136-300-175A.

.2	Test prior to commencement of asbestos removal.

.3	Use only negative air units and HEPA vacuums tested and inspected as specified.

.4	Monitor air inside asbestos control area to ensure that fibre levels are within acceptable limits required by Alberta Occupational Health and Safety Act and Chemical Hazards Regulation for type of respirators being used.

1.11	AIRBORNE FIBRE LEVELS

.1	In areas outside asbestos control area and where full containment procedures are not required, airborne fibre levels shall not exceed 0.01 fibers per cubic centimeter of air.

.2	In areas inside asbestos control area where full containment procedures are followed, airborne fibre levels shall not exceed acceptable limits for type of respirators being used.

1.12	PROTECTION OF PERSONNEL

.1	Provide workers with respirators and hooded disposable coveralls conforming to Occupational Health and Safety Regulations for the airborne asbestos fibre levels that are present during asbestos control work.

.2	Do not permit smoking, eating or drinking in work area.

.3	Provide the following to employees involved in asbestos control work:

.1	Written information describing potential health hazards related to exposure to asbestos fibre.

.2	Written instructions describing safe work procedures.

.4	Where full containment procedures are not required, do the following:

.1	Comply with regulatory requirements.

.2	Provide workers with not less than a non-powered half-mask respirator equipped with P100 filters and hooded disposable coveralls.  Coveralls shall fit snugly around neck, wrists and ankles.

.3	Allow no one in the removal area during asbestos control work unless wearing disposable coveralls and respirator equipped with P100 filters.

.5	Provide the following safety equipment for Minister's representatives, as required to permit ready and safe access to the work:

.1	Disposable or cloth coveralls.

.2	Rubber boots or easily decontaminated footwear.

.3	Caps.

.4	Eye protection.

.5	Gloves.

.6	Hard hats.

.7	Non-powered half mask respirator equipped with P100 filters (minimum).

2.	Products

2.1	MATERIAL AND EQUIPMENT

.1	Asbestos Sealer:  to CAN/CGSB-1.205-94, Sealer for Application to Asbestos-Fibre-Releasing Materials, Class A - water-based, for spray application, and as follows:

.1	Type 1 – Penetrating.  Acceptable products:  American Coating “CC-22P”, Better Working Environments “BWE 3000”, Certified Technologies “Undercoat 2050” Childers “Chil-Abate CP-210”, Fiberlock Technologies “ABC”, Foster “32-20 (yellow), 32-21(blue), 32-22(undyed)”, International Protective Coatings “Serpilock, Serpiflex Shield”.

.2	Type 2 - Surface Film Forming.  Acceptable products:  American Coating “CC-2B”, Certified Technologies “Overcoat 2000”, Childers “Chil-Bridge CP-211”, Fiberlock Technologies “ABC”, Foster “32-32”, International Protective Coatings “Serpiflex Shield”.

.2	Vacuums:  HEPA filtered wet/dry type, with accessories adequate to perform removal and cleanup work.

2.2	ASBESTOS DISPOSAL CONTAINERS

.1	Plastic Bags:  to CAN/CGSB-43.150, minimum 150 micrometer thick sheet polyethylene.  Bag seams shall be sufficiently strong to resist pressure and shocks that occur under normal conditions of transport.  Designed and manufactured to contain a maximum net mass of 50kg.

.2	Drums:  to CAN/CGSB-43.150, sturdy non-reusable, steel (1A2), aluminum (1B2), or plastic (1H2), with tight fitting lids.

.3	Sheet Polyethylene:  two separate layers, minimum 150 micrometer thick, each layer sealed with water-resistant plastic duct tape.

.4	Label containers with labels stating "CONTAINS ASBESTOS, CANCER HAZARD, AVOID BREATHING DUST".

2.3	WARNING SIGNS

.1	Provide warning signs which state that:

.1	Asbestos is present in the area.

.2	Access to the area is prohibited, except to authorized personnel.

.3	Drinking, eating and smoking are prohibited in the area.

.2	Obtain Minister's approval of warning sign wording, legibility and location.

3.	Execution

3.1	PREPARATION

.1	Asbestos control work may commence only after the following have been completed:

.1	Existing property, including non-removable equipment and furnishings, surfaces and finishes, have been protected from damage and contamination due to asbestos control work.

.2	HVAC system has been [deactivated] [isolated] and sealed to prevent asbestos fibres from entering the system.

.3	Electrical system has been isolated.

.4	Barriers are in place.

.5	Decontamination facilities are in place and operational.

.6	Negative pressure ventilation system has been installed and certified acceptable by testing agency.

.7	Warning signs have been placed around perimeter of asbestos control area and at each potential entrance to the area.

.8	Minister has inspected and approved preparations.

OR

SPEC NOTE:  Delete above clauses and specify the following if full containment procedures are not specified.

.1	Asbestos control work may commence only after the following have been completed:

.1	Existing property, including non-removable equipment and furnishings, surfaces and finishes, have been protected from damage and contamination due to asbestos control work.

.2	Barriers are in place and work area has been isolated.

.3	Warning signs have been placed around perimeter of asbestos control area and at each potential entrance to the area.

.4	Minister has inspected and approved preparations.

3.2	ASBESTOS [REMOVAL] [ENCAPSULATION]

SPEC NOTE:  Edit this article to suit scope of asbestos control work.

.1	Refer to Section 13283 for asbestos removal requirements.

.2	Refer to Section 13284 for asbestos encapsulation requirements.

3.3	PREPARATION FOR ASBESTOS DISPOSAL

.1	Prepare [contaminant and] contaminated materials for disposal as follows:

.1	Place in double bagged plastic asbestos disposal bags or inside disposable drums with tight fitting lids.

.2	Wrap bulk materials that do not lend themselves to disposal in plastic bags or drums, in sheet polyethylene.  (2 separately sealed layers)

.3	The resulting package must be constructed, filled and closed so that, under normal conditions of handling and transport, there will be no discharge, emission or escape of the dangerous goods form the package or small container that could constitute a danger to public safety.

.2	Transfer asbestos waste containers and normal construction waste from asbestos control area for disposal, in accordance with procedures described in the following documents.

.1	Alberta Environmental Protection document entitled “Guidelines for the Disposal of Asbestos Waste”.

.2	Alberta Employment, Immigration and Industry document entitled “Asbestos Abatement Manual”, current edition.

.3	Section 13283 – Asbestos Removal.

.4	Where more than one document addresses an issue, the most stringent requirements shall apply.

.3	Treat contaminated water as asbestos waste.

3.4	DISPOSAL OF NORMAL CONSTRUCTION WASTE

.1	This article applies to materials not readily prepared for asbestos disposal as specified, and being capable of thorough cleaning, for example, bulky mechanical equipment.

.2	Clean materials until free of visible asbestos, wash, and dip in or spray with asbestos sealer.

.3	Dispose of as normal construction waste.

3.5	TRANSPORTATION AND PERMANENT DISPOSAL of ASBESTOS WASTE

.1	Transport asbestos waste in accordance with Alberta and Federal legislation and regulations.

.2	Ensure that all materials are properly packaged and labeled prior to transportation.  Each container must be marked in accordance with the Dangerous Goods Transportation and Handling Act showing the shipping name [(Blue or Brown Asbestos)] [(White Asbestos)] and product identification number [(UN2212)] [(UN2590)].

SPEC NOTE:  Blue Asbestos or Brown Asbestos  UN2212,  White Asbestos UN2590

.3	Transport hazardous waste materials in properly placarded vehicles.

.4	Transport asbestos waste in a manner which will prevent asbestos fibres from becoming airborne.

.5	Each load shall be accompanied by a properly completed manifest satisfactory to the authority having jurisdiction.

.6	Dispose of asbestos waste in a supervised, approved sanitary landfill site.

.7	Make arrangements with operator of landfill site in advance to receive asbestos waste material.

.8	In event of leakage or spillage enroute, repackage material before continuing transport to landfill.

.9	If spill, emission or discharge of waste asbestos is in excess of 50 kg from the transport unit, immediately report the incident to the local police.

.10	Place asbestos waste containers intact in excavated area.  Do not dump or throw containers from truck.  Repackage contents of containers that have broken open, in accordance with requirements for preparation for asbestos disposal.

.11	Arrange for asbestos waste to be covered with soil.

.12	Provide the Minster with a copy of each waste manifest once asbestos waste has been disposed of at a supervised, approved landfill site.

3.6	WORKER DECONTAMINATION

.1	Workers shall follow decontamination procedures as outlined in the "Manual of Safe Practice" [and as specified].

SPEC NOTE:  Delete remainder of this article if glovebag removal method is not a Contractor option.

.2	Prior to leaving area where asbestos has been removed by method not requiring full containment, vacuum using HEPA filtered vacuum or wet wipe in coveralls.  Dispose of coveralls and wiping rags into polyethylene bags as asbestos waste.

.3	Immediately upon leaving area where asbestos has been removed by method not requiring full containment, perform the following:

.1	Proceed to nearest shower outside work area and, with respirator in place, shower head and face prior to removal of respirator.  If a shower is not available, wash head thoroughly, including exterior of respirator, prior to removing respirator.

.2	Dispose of respirator filters as asbestos waste.

3.7	DAILY CLEANING

.1	Progressively containerize contaminant and contaminated material as removal work progresses.  Do not permit asbestos waste to accumulate.

.2	Keep contaminant and contaminated material damp to minimize generation of airborne asbestos fibres.

.3	Remove asbestos waste from asbestos control area at least once per day.

.4	Regularly check, clean and replace filters as necessary.

3.8	FINAL CLEANING

.1	Upon completion of asbestos control work, perform the following:

.1	Remove asbestos waste from work site.

.2	Vacuum and wash contaminated tools and equipment.

.3	Dispose of non-reusable materials and contaminated materials as asbestos waste.

.4	Clean site to original condition.

.5	Make good any damage resulting from the asbestos control work, to the satisfaction of the Minister.

END OF SECTION