Section Cover Page

Section 13282 2002-01-02 Asbestos Containment Procedures

Use this Section where full containment will be required, or if a Contractor option, may be required, depending on the removal method(s) selected by the Contractor.

Do not use this Section if full containment procedures are normally not required for the removal procedures specified.

Edit this Section only in consultation with Alberta Infrastructure specialists in asbestos control procedures.

Use this Section in conjunction with Section 13281 - Asbestos Control General Requirements, with Section 13283 - Asbestos Removal, and with Section 13284 - Asbestos Encapsulation.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Intent

1.2	Section Includes

  - Related Sections

  - Reference Standards

1.5	Definitions

1.6	Fire Regulations

2.	Products

2.1	Barriers Materials

2.2	Equipment

2.3	Decontamination Facilities

2.4	Negative Pressure Ventilation System

3.	Execution

3.1	HVAC System Deactivation

3.2	HVAC System Isolation

3.3	Electrical System Isolation

3.4	Installation of Barriers

3.5	Removal of Barriers

The reference standards specified in Article 1.4 may be available for reference purposes in the Technical Resources and Standards Division Library, Alberta Infrastructure, 3rd Floor, 6950 - 113 Street, Edmonton; Telephone: (780) 427-7924.

1.	General

1.1	INTENT

.1	Read this Section in conjunction with Section 13281 - Asbestos Control General Requirements.

1.2	SECTION INCLUDES

.1	This Section includes requirements for:

.1	Isolation of asbestos control area from other building space [, and the exterior environment],

.2	Measures to maintain asbestos fibre levels inside and outside of asbestos control areas to acceptable levels, and,

.3	Measures to control transfer of materials and personnel in and out of asbestos control area, to minimize escape of asbestos fibres from the control area.

1.3	RELATED SECTIONS

.1	Rough Carpentry:	Section 06100.

.2	Asbestos Removal:	Section 13283.

.3	Asbestos Encapsulation:	Section 13284.

.4	[              ]:	[             ].

1.4	reference Standards

SPEC NOTE:  Edit this Article to suit applicable standards referenced in this section.  Add or delete as required.

- CAN/CGSB-51.34-M86 - Vapour Barrier, Polyethylene Sheet for Use in Building Construction.

.2	CSA O121-M1978 (R1999) – Douglas Fir Plywood.

.3	CAN/CSA-O141-91 (R1999) – Softwood Lumber.

.4	CSA O151-M1978 (R1999) – Canadian Softwood Plywood.

.5	CSA O153-M1980 (R1998) – Poplar Plywood.

.6	CSA )437 Series 93 – Standards on OSB and Waferboard

.7	National Lumber Grades Authority (NGLA), latest edition – Standard Grading Rules for Canadian Lumber.

1.5	DEFINITIONS

.1	Barrier:  means construction designed to isolate and seal asbestos control area from remainder of building [and from the exterior environment] before, during, and after asbestos control work.

1.6	FIRE REGULATIONS

.1	Comply with requirements of authority having jurisdiction over fire safety, including the following:

.1	Location of emergency and fire exits from the work area.

.2	On-site fire fighting equipment.

2. 	Products

2.1	BARRIER MATERIALS

.1	Sheet Material for Walls and Ceilings:  polyethylene, to CAN/CGSB-51.34, minimum 150 micrometre thick.

.2	Sheet Material for Floors:  sheet polyethylene, glass fibre reinforced, minimum 250 micrometre thick.

.3	Dimension Board Lumber:  to CAN/CSA-0141 and graded in accordance with current National Lumber Grades Authority (NLGA) Standard Grading Rules for Canadian Lumber.

.1	Moisture Content:  maximum 19% at time of installation.

.2	Surface Finish:  S4S for members receiving finishes, S2S or S4S for members not receiving finishes.

.4	Wood Panel Products:

.1	Canadian Softwood Plywood:  to CSA 0151.

.2	Douglas Fir Plywood:  to CSA 0121.

.3	Poplar Plywood:  to CSA 0153.

.4	Waferboard and Oriented Strand Board:  to CSA 0437.

.5	Tape:  moisture-resistant duct tape.

2.2	EQUIPMENT

.1	Negative Air Units:  two-stage HEPA filter system and accessories required to exhaust air to outside of building.

2.3	DECONTAMINATION FACILITIES

SPEC NOTE:  If tender documents provide detailed documentation required under Asbestos Control Plan, edit this article accordingly.

.1	Decontamination facilities shall include:

.1	Clean change room.

.2	Showers.

.3	Asbestos waste transfer rooms.

.4	Protective equipment storage.

.5	[Toilet facilities.]

SPEC NOTE:  If possible and practicable, specify Contractor's use of existing toilet facilities located outside asbestos control area.  Specify in Division 1.

.2	Provide minimum number of entrances into decontamination facility from outside asbestos control work area.

.3	Obtain Minister's approval of location and construction of decontamination facility prior to commencement of work.

.4	Provide adequate facilities for storage of protective equipment in decontamination facility.

.5	Hot and cold water supply lines shall have water shut-off valve located outside of asbestos control area.

2.4	NEGATIVE PRESSURE VENTILATION SYSTEM

.1	Provide negative pressure ventilation system that is separate from building mechanical system.

.2	System shall include:

.1	Make-up air drawn through decontamination facility.

.2	Exhaust air vented to building exterior through negative air units.

.3	System shall:

.1	be capable of changing total volume of air in the containment area four times per hour, and

.2	maintain a negative pressure of 5 Pa across the barrier between the clean area and the asbestos control area.

.4	Start operation of negative air system before beginning asbestos control work.  Operate continuously until asbestos control work has been completed and fibre levels stabilize at levels acceptable to Minister.

.5	Monitor condition of filters on a regular basis and replace filters as required to maintain air changes and negative pressure.

.6	Provide separate makeup air ducting and combustion air ducting to prevent backdrafting or damage to boilers, hot water heaters or any other gas fired equipment that is required to remain operational during asbestos removal work.

3.	Execution

3.1	HVAC SYSTEM DEACTIVATION

.1	Shut down entire building HVAC system.

.2	Seal openings to HVAC system to prevent asbestos fibres from entering system.

.3	Coordinate mechanical system deactivation with Minister.

OR

SPEC NOTE:  Specify either "HVAC System Deactivation" or "HVAC System Isolation".  Specify both only if project is phased and both are applicable.

3.1	HVAC SYSTEM ISOLATION

.1	Shut down HVAC system to asbestos control area.

.2	Seal openings to HVAC system to prevent asbestos fibres from entering system.

.3	Coordinate mechanical system isolation with Minister.

3.2	ELECTRICAL SYSTEM ISOLATION

.1	Isolate electrical systems which will remain energized in the asbestos control area, with ground fault interrupters.

.2	Use only ground fault protected electrical services for electrical equipment used in the asbestos control area.

.3	Coordinate electrical system isolation with Minister.

3.3	INSTALLATION OF BARRIERS

.1	Isolate asbestos work area from remainder of building.

.2	Seal off openings in the perimeter including, but, not limited to, the following:

.1	Heating and ventilation grills and outlets.

.2	Doorways.

.3	Elevator shafts.

.4	Corridors.

.5	Openings for lighting and electrical systems.

.6	Sleeves in ceiling space and floors, above and below work area.

.3	Use barrier materials to construct entrances, exits and transfer openings to decontamination area, in an arrangement to form an airlock between doors.  Door arrangement shall meet the following criteria:

.1	One door shall always be closed as workers pass through entry system.

.2	Under negative pressure, supply air can be drawn in through the entry system.

.3	In the event of loss of negative pressure, door systems shall seal to prevent airborne fibres from escaping asbestos control area.

.4	Seal HVAC supply and return air louvres, [elevator doorways] and grilles to prevent contamination of the system.  Cover louvres and grilles with rigid material such as plywood or sheet metal, and seal with two layers of polyethylene.  Obtain Minister's approval prior to using an alternative sealing method.

.5	Protect walls within work area with polyethylene sheeting mechanically fastened at the top and bottom of the wall.  Seal joints with tape.

.6	Construct free standing barriers as required, running from floor to underside of structure above, using wood or steel studs spaces at maximum 600 mm on centre with polyethylene sheeting. Seal joints and perimeter with tape.

.7	After penetrations through floors have been sealed, protect floors with one layer of fibre-reinforced polyethylene.  Seal joints and perimeter with tape.

.8	Protect wall-mounted equipment from asbestos contamination by sealing with polyethylene.  Where equipment is left exposed, thoroughly clean after completion of asbestos control work.

SPEC NOTE:  Specify additional requirements for unique circumstances and conditions.

.9	[                                    ].

3.4	REMOVAL OF BARRIERS

.1	Upon completion of asbestos control work, perform the following:

.1	Wipe down and spray polyethylene sheets used to protect walls and floor, using sealer.

.2	Remove polyethylene wall sheets when air-borne asbestos fibre concentration has reached an acceptable level.  Minister will advise when fibre concentrations are low enough to remove sheeting.

.3	Carefully fold sheets with asbestos exposed side folded in.  Dispose of as asbestos waste.

.2	Remove other barrier materials from site.

END OF SECTION