Section Cover Page

Section 15060 2000-06-01 Hangers and Supports

This Master Specification Section contains:

.1	This Cover Sheet

.2	Data Sheet – Reference Standards

.3	Specification Section Text:

1.	General

1.1	Products Supplied But Not Installed Under This Section

1.2	Reference Documents

1.3	General Requirements

1.4	Approvals

2.	Products

2.1	Inserts

2.2	Pipe Hangers and Supports

2.3	Hanger Rods

2.4	Duct Hangers and Supports

2.5	Flashing

2.6	Sleeves

2.7	Finishes on Hanger Rods, Hangers and Supports

3.	Execution

3.1	Inserts

3.2	Pipe Hangers and Supports

3.3	Low Velocity Duct Hangers and Supports

3.4	Medium and High Velocity Duct Hangers and Supports

3.5	Equipment Bases and Supports

3.6	Flashing

3.7	Sleeves

Applicable Standards

.1	ANSI/ASME B31.1-1995	Power Piping

.2	ASTM A653M-96	Sheet Steel, Zinc Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot Dip Process

.3	CAN/CGSB-1.40-M89	Primer, Structural Steel, Oil Alkyd Type

.4	NFPA13-1996	Installation of Sprinkler Systems

.5	NFPA14-1996	Installation of Standpipe and Hose Systems

These reference documents may be available for reference purposes in the Technical Resources and Standards Branch Library, Alberta Infrastructure, 3rd Floor, 6950 - 113 Street, Edmonton; Telephone:  (780) 427-7924.

END OF DATA SHEET

1.	General

1.1	PRODUCTS SUPPLIED BUT NOT INSTALLED UNDER THIS SECTION

SPEC NOTE:  Delete this article if roof drains are not specified.  Refer to applicable roofing specification Section for installation of lead flashings and strip-in type plumbing flashings.

.1	Lead flashings for roof drains, for installation under Section [07510] [    ].

1.2	REFERENCE DOCUMENTS

.1	Pipe supports shall meet the requirements of ANSI/ASME B31.1-1995, Power piping.

.2	Automatic sprinkler pipe supports shall meet the requirements of NFPA 13-1996, Standard for the Installation of Sprinkler Systems.

.3	Standpipe and hose system pipe supports shall meet the requirements of NFPA14-1996, Standard for the Installation of Standpipe and Hose Systems.

.4	Duct hangers shall follow the recommendations of the SMACNA Duct Manuals.

1.3	GENERAL REQUIREMENTS

.1	Provide hangers and supports to secure equipment in place, prevent vibration, maintain grade, provide for expansion and contraction and to accommodate insulation; provide insulation protection saddles.

.2	Install supports of strength and rigidity to suit loading without unduly stressing building.  Locate adjacent to equipment to prevent undue stresses in piping and equipment.

.3	Select hangers and supports for the service and in accordance with the manufacturer's recommended maximum loading.  Hangers shall have a safety factor of 5 to 1.

.4	Fasten hangers and supports to building steel or inserts in concrete construction.

.5	Provide and set sleeves required for equipment, including openings required for placing equipment.

.6	Dielectrically isolate dissimilar metals.

1.4	APPROVALS

.1	Obtain approval from the Minister prior to drilling for inserts and supports for piping systems.

.2	Obtain approval from the Minister prior to using percussion type fastenings.

.3	Use of existing piping or equipment for hanger supports is not permitted.

.4	Use of perforated band iron, wire or chain as hangers is not permitted.

2.	Products

2.1	INSERTS

.1	Inserts shall be malleable iron case or [galvanized] steel shell and expander plug for threaded connection with lateral adjustment, top slot for reinforcing rods, lugs for attaching to forms.

.2	Size inserts to suit threaded hanger rods.

2.2	PIPE HANGERS AND SUPPORTS

.1	Hangers:  Pipe sizes 15 mm to 40 mm:  Adjustable wrought steel ring.

.2	Hangers:  Pipe sizes 50 mm to 100 mm and Cold Pipe Sizes 150 mm Over:  Adjustable wrought steel clevis.

.3	Hangers:  Hot Pipe Sizes 150 mm and Over:  Adjustable steel yoke and cast iron roll.

.4	Multiple or Trapeze Hangers:  Steel channels with welded spacers and hanger rods, cast iron roll and stand for hot pipe sizes 150 mm and over.

.5	Wall Support:  Pipe Sizes to 80 mm:  Cast iron hook.

.6	Wall Support:  Pipe Sizes 100 mm and Over:  Welded steel bracket and wrought steel clamp, adjustable steel yoke and cast iron roll for hot pipe sizes 150 mm and over.

.7	Vertical Support:  Steel riser clamp.

.8	Floor Support:  Pipe Sizes to 100 mm and All Cold Pipe Sizes:  Cast iron adjustable pipe saddle, locknut nipple, floor flange and concrete pier to steel support.

.9	Floor Support:  Hot Pipe Sizes 150 mm and over:  Adjustable cast iron roll and stand, steel screws and concrete pier or steel support.

.10	Design hangers so they cannot become disengaged by movements of supported pipe.

.11	Provide copper plated hangers and supports for copper piping or provide sheet lead packing between hanger or support and piping.

.12	Insulate aluminum piping from dissimilar metal supports.

2.3	HANGER RODS

.1	Provide steel hanger rods, threaded both ends, threaded one end, or continuous threaded.

2.4	DUCT HANGERS AND SUPPORTS

.1	Hangers:  Galvanized steel band iron or rolled angle and 10 mm rods.

.2	Wall Supports:  Galvanized steel band iron or fabricated angle bracket.

.3	Vertical Support at Floor:  Rolled angle.

2.5	FLASHING

.1	Steel Flashing:  0.55 mm galvanized steel.

.2	Lead Flashing:  sheet lead, as follows:

.1	For Waterproofing:  25 kg/m2.

.2	For Soundproofing:  5 kg/m2.

.3	Lead Sheet Size:

.1	Roof Drains:  minimum 810 mm x 810 mm.

.2	Roof Plumbing Vents:  as required to provide base flashing overlap to ARCA detail.

.3	Floor Drains:  minimum 920 x 920 mm and as specified.

.4	Other Locations:  as specified.

.3	Safes:  25 kg/m2 sheet lead or 200 micrometre neoprene.

.4	Caps:  Steel, 0.70 mm thickness minimum, 1.6 mm thickness at  fire resistance structures.

2.6	SLEEVES

.1	Pipes through Floors:  Form with 1.2 mm galvanized steel.

.2	Pipes through Beams, Walls, Fire Proofing, Footings, Potentially Wet Floor:  Form with steel pipe or 1.2 mm thickness galvanized steel.

.3	Roof Drains:  form sleeves with 0.7 mm thick sheet steel galvanized with Z275 zinc coating to  ASTM A653M-96.  Refer to Detail Drawings appended to Section specifying roofing membrane.

SPEC NOTE:  Verify that detail drawings indicate drain sleeves.

.4	Round Ducts:  Form sleeves with galvanized steel.

.5	Rectangular Ducts:  Form sleeves with galvanized steel or wood.

.6	Size large enough to allow for expansion with continuous insulation.

2.7	FINISHES ON HANGER RODS, HANGERS AND SUPPORTS

.1	All steel hanger rods, hangers and supports shall be galvanized or factory primed with alkyd red oxide primer to CAN/CGSB-1.40-M89.

3.	Execution

3.1	INSERTS

.1	Use inserts for suspending hangers from reinforced concrete slabs and sides of reinforced concrete beams wherever practicable.

.2	Set inserts in position in advance of concrete work. Provide reinforcement rod in concrete  for  inserts carrying piping over 100 mm or ducts over 1500 mm wide.

.3	Where concrete slabs form finished ceiling, finish inserts flush with slab surface.

.4	Where inserts are omitted, drill through concrete slab from below and provide rod with recessed square steel plate and nut above slab.

3.2	PIPE HANGERS AND SUPPORTS

.1	Support horizontal steel and copper piping as follows:

| Nominal Pipe Size | Distance Between Supports | Hanger Rod Diameter |
| --- | --- | --- |
| 15 mm | 1.8 m | 10 mm |
| 20 mm to 40 mm | 1.8 m | 10 mm |
| 50 mm & 65 mm | 3 m | 10 mm |
| 80 mm & 100 mm | 3.6 m | 16 mm |
| 150 mm to 300 mm | 4.3 m | 22 mm |
| 350 mm to 450 mm | 6.1 m | 25 mm |

.2	Install hangers to provide minimum 12 mm clear space between finished covering and adjacent work.

.3	Place a hanger within 300 mm of each horizontal elbow.

.4	Use hangers which are vertically adjustable 40 mm minimum after piping is erected.

.5	Support horizontal soil pipe near each hub with 1.5 m maximum spacing between hangers.

.6	Support vertical piping at every other floor.  Support vertical soil pipe at each floor at hub.

.7	Where several pipes can be installed in parallel and at same elevation, provide multiple or trapeze hangers.

.8	Where practical, support riser piping independently of connected horizontal piping.

3.3	LOW VELOCITY DUCT HANGERS AND SUPPORTS

.1	Hanger Minimum Sizes:

.1	Up to 750 mm wide:  25 x 1.6 mm at 3 m spacing.

.2	790 to 1200 mm wide:  40 x 1.6 mm at 3 m spacing.

.3	Over 1200 mm wide:  40 x 1.6 mm at 2.4 m spacing.

.2	Horizontal Duct on Wall Supports Minimum Sizes:

.1	Up to 450 mm wide:  40 x 1.6 mm or 25 x 25 x 3 mm at 2.4 m spacing.

.2	480 x 1000 mm wide:  40 x 40 x 3 mm at 1.2 m spacing.

.3	Vertical Duct on Wall Supports Minimum Sizes at 3.65 m spacing:

.1	Up to 610 mm wide:  40 x 1.6 mm.

.2	640 to 900 mm wide:  25 x 25 x 3 mm.

.3	Over 1520 mm wide:  50 x 3 mm.

.4	940 to 1200 mm wide:  30 x 30 x 3 mm.

.4	Vertical Duct Floor Supports Minimum Sizes, riveted or screwed to ducts:

.1	Up to 1520 mm wide:  40 x 40 x 3 mm.

.2	Over 1520 mm wide:  50 x 3 mm.

3.4	MEDIUM AND HIGH VELOCITY DUCT HANGERS AND SUPPORTS

.1	Hanger Minimum Sizes:

.1	Up to 900 mm wide:  2 at 25 x 1.6 mm at 3 m spacing.

.2	940 x 1520 mm wide:  2 at 25 x 1.6 mm at 2.4 m spacing and 50 x 50 x 6 mm trapeze.

.3	1550 x 3050 mm wide:  2 at 38 x 2.6 mm at 2.4 m spacing and 50 x 50 x 7 mm trapeze.

.4	3070 x 6700 mm wide:  3 at 10 mm diameter at 1.2 m spacing and 65 x 65 x 5 mm trapeze.

.2	Round Duct Hangers Minimum Sizes at 3 m spacings:

.1	Up to 460 mm diameter:  25 x 1.6 mm.

.2	480 to 900 mm diameter:  25 x 2.6 mm.

.3	940 to 1270 mm diameter:  40 x 2.6 mm.

.4	1300 to 2130 mm diameter:  2 at 40 x 2.6 mm from girth reinforcing angle.

.3	Vertical Duct Floor Supports Minimum Sizes:

.1	Up to 1220 mm wide:  40 x 40 x 3 mm.

.2	Over 1220 mm wide:  50 x 50 x 30 mm.

.3	Rivet to duct and tie angles together with rod, angles or band Iron.

.4	Angle reinforcing may be used for support omitting trapeze.

3.5	EQUIPMENT BASES AND SUPPORTS

.1	Provide for major equipment, reinforced concrete housekeeping bases poured directly on structural floor slab 100 mm thick minimum, extended 100 mm minimum beyond machinery bedplates.  Provide templates, anchor bolts and accessories required for mounting and anchoring equipment.

.2	Construct supports of structural steel members or steel pipe and fittings.  Brace and fasten with flanges bolted to structure.

.3	Rigidly anchor ducts and pipes immediately after vibration connections to equipment.

3.6	FLASHING

.1	Flash and counterflash where mechanical equipment passes through weather or waterproofed walls, floors, and roofs.

.2	Flash vent and soil pipes projecting 75 mm minimum above roof membrane with lead worked 25 mm minimum into hub, 200 mm minimum clear on sides.  For pipes through outside walls turn flange back into wall and caulk.

.3	Flash floor drains over finished areas with lead minimum 250 mm clear on sides.  Fasten flashing to drain clamp device.

.4	Provide curbs for mechanical roof installations, minimum 200 mm high.

.5	Attach counterflashings to mechanical equipment and lap base flashings on roof curbs.

.6	All joints in counterflashings shall be flattened and soldered double seam.  Storm collars shall be adjustable to draw tight to pipe with bolts.  Caulk around the top edge.  Use storm collars above all roof jacks.

.7	Screw vertical flange section of roof jacks to face of curb.

.8	Provide continuous lead or neoprene safes below [air supply casings,] [built-up mop sinks,] [shower stalls], [shower room] floors located above finished rooms.  Solder at joints, flash into floor drains and turn up 150 mm into walls or to top of curbs and caulk into joints.

.9	Provide lead flashing around ducts and pipes passing from equipment rooms, installed according to manufacturer's data for sound control.

.10	Cut openings in lead flashings installed over roof drains and work down lead into drain body as indicated on detail drawings appended to roofing specification.

3.7	SLEEVES

.1	Set sleeves in position in advance of concrete work.  Provide suitable reinforcing around sleeves.

.2	Extend sleeves through potentially wet floors 25 mm above finished floor level.  Caulk sleeves full depth and provide floor plate.

.3	Where piping or ductwork passes through floor, ceiling or wall, close off space between pipe or duct and construction with non-combustible insulation.  Provide tight fitting metal caps on both sides and caulk.

.4	Install chrome plated escutcheons where piping passes through finished surfaces.

END OF SECTION