Section Cover Page

Section 15082 2000-06-01 Piping and Equipment Insulation

Use this Section to specify requirements for Piping and Equipment Insulation.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Data Sheet - Reference Standards

.3	Data Sheet - Product Selection and Specification

.4	Specification Section Text:

1.	General

1.1	Related Requirements

1.2	Product Options and Substitutions

1.3	Shop Drawings and Product Data

1.4	Definitions

1.5	Flame/Smoke Development Ratings

2.	Products

2.1	Hot Pipe Insulation

2.2	Hot Equipment Insulation

2.3	Engine Exhaust Insulation

2.4	Cold Pipe Insulation

2.5	Cold Equipment Insulation

2.6	Accessories

2.7	Recovery Materials

3.	Execution

3.1	Installation, General

3.2	Hot Pipe Insulation Application

3.3	Hot Equipment Insulation Application

3.4	Engine Exhaust Insulation Application

3.5	Cold Pipe Insulation Application

3.6	Cold Equipment Insulation Application

3.7	Insulation Type Thickness Schedule

Applicable Standards:

.1	ASTM C411-82 (1992)el	Hot-Surface Performance of High Temperature Thermal Insulation.

.2	ASTM E84-96a	Surface Burning Characteristics of Building Materials

.3	CAN/CGSB-51.2-95	Calcium Silicate Thermal Insulation, for Piping, Machinery and Boilers

.4	CAN/CGSB-51.9-92	Mineral Fiber Thermal Insulation for Piping and Round Ducting

.5	CAN/CGSB-51.10-92	Mineral Fiber Board Thermal Insulation

.6	CAN/CGSB-51.11-92	Mineral Fiber Thermal Insulation Blanket

.7	CAN/CGSB-51.12-95	Thermal Insulating and Finishing Cement

.8	CAN/CGSB-51.40-95	Flexible, Elastomeric, Unicellular Thermal Insulation, Sheet and Pipe Covering

.9	CGSB 51-GP-52Ma	Vapour Barrier, Jacket and Facing Material for Pipe, Duct and Equipment Thermal Insulation

.10	CAN/CGSB-51.53-95	Poly (Vinyl Chloride) Jacketing Sheet for Insulated Pipes, Vessels and Round Ducts

.11	NFPA 255-1996	Method of Test of Surface Burning Characteristics of Building Materials

.12	CAN/ULC-S102-1988	Surface Burning Characteristics of Building Materials and Assemblies

These reference documents may be available for reference purposes in the Technical Resources and Standards Branch Library, Alberta Infrastructure, 3rd Floor, 6950 - 113 Street, Edmonton; Telephone:  (780) 427-7924.

Consider carefully all requirements relating to recovering of exposed insulation surfaces.  Specify recovering materials as follows:

.1	Canvas:  if surfaces are to be painted.

.2	PVC:  if surfaces are subject to damage or abuse.

.3	Aluminum:  if surfaces are subject to damage or abuse or where appearance is important.

END OF DATA SHEETS

1.	General

1.1	RELATED REQUIREMENTS

.1	Mechanical General Requirements:	Section 15010.

1.2	PRODUCT OPTIONS AND SUBSTITUTIONS

.1	Refer to Division 1 for requirements pertaining to product options and substitutions.

1.3	SHOP DRAWINGS AND PRODUCT DATA

.1	Comply with requirements of Section 15010.

.2	Submit an insulation schedule, for each application include the following information:

.1	Materials

.2	"k" value

.3	Thickness

.4	Density

.5	Finish

.6	Jacketing

.3	Submit product data and test reports when requested to substantiate that insulation and recovery assemblies meet flame/smoke development ratings and performance requirements for the assembly and thickness used.

1.4	DEFINITIONS

.1	For the purposes of this Section, the following definitions apply:

.1	Concealed:  piping systems and equipment in trenches, shafts, furring, and suspended ceilings.

.2	Exposed:  piping systems and equipment in mechanical rooms or otherwise not "concealed".

.3	"k" Value:  thermal conductivity of insulating material per unit of thickness (W/m.°C).

1.5	FLAME/SMOKE DEVELOPMENT RATINGS

.1	Pipe insulations, recovery materials, tapes, vapour barrier facings and adhesives shall have maximum flame spread rating of 25 and maximum smoke developed rating of 100 except in plenum spaces and air handling systems where maximum smoke development rating shall be 50, when tested in accordance with CAN/ULC-S102-1988, NFPA 255-1996, or ASTM E84-96a.

SPEC NOTE:  Specify smoke development of 50 when a building is classified as a "high rise".

.2	Insulating materials and accessories shall withstand service temperatures without smoldering, glowing, smoking or flaming when tested in accordance with ASTM C441-82.

2.	Products

2.1	HOT PIPE INSULATION

.1	Hot Pipe Insulation - Mineral Fibre:

.1	Material:  formed rigid mineral fibre insulation sleeving to CAN/CGSB-51.9-92.

.2	"k" Value:  maximum 0.035 W/m.°C at 24°C mean temperature.

.3	Service Temperature:  up to 150°C.

.4	Jacket:  factory applied general purpose jacket.

.2	Hot Pipe Insulation - Black Rubber:

.1	Material:  flexible elastomeric unicellular preformed pipe covering to CAN/CGSB-51.40-95.

.2	"k" Value:  0.04 W/m. °C at 24°C mean temperature.

.3	Service Temperature:  up to 100°C.

.4	Maximum Allowable Thickness:  25 mm.

2.2	HOT EQUIPMENT INSULATION

.1	Hot Equipment Insulation - Flat Surfaces:

.1	Material:  rigid mineral fibre to CAN/CGSB-51.10-92.

.2	"k" Value:  maximum 0.035 W/m.°C at 24°C mean temperature.

.3	Service Temperature:  20°C to 120°C.

.2	Hot Equipment Insulation - Curved Surfaces:

.1	Material:  mineral fibre blanket to CAN/CGSB-51.11-92.

.2	"k" Value:  maximum 0.035 W/m.°C at 24°C mean temperature.

.3	Service Temperature:  20°C to 120°C.

2.3	ENGINE EXHAUST INSULATION

.1	Material:  formed rigid hydrous calcium silicate for piping to CAN/CGSB-51.2-95.

.2	"k" Value:  maximum 0.059 W/m.°C at 93°C mean temperature.

.3	Service Temperature:  up to 750°C.

2.4	COLD PIPE INSULATION

.1	Cold Pipe Insulation:  Mineral Fibre:

.1	Material:  formed mineral fibre rigid insulation sleeving to CAN/CGSB-51.9-92.

.2	"k" Value:  maximum 0.035 W/m.°C at 24°C mean temperature.

.3	Service Temperature:  -14°C to 100°C.

.4	Jacket:  factory applied vapour barrier jacket to CGSB 51-GP-52Ma, Type 1, with longitudinal lap seal.

.2	Cold Pipe Insulation - Black Rubber:

.1	Material:  flexible elastomeric unicellular preformed pipe covering to CAN/CGSB-51.40-95.

.2	"k" Value:  0.04 W/m. °C at 24°C mean temperature.

.3	Service Temperature:  -4°C to 100°C.

.4	Maximum Allowable Thickness:  25 mm.

2.5	COLD EQUIPMENT INSULATION

.1	Cold Equipment Insulation - Flat Surfaces:

.1	Materials:  rigid mineral fibre to CAN/CGSB-51.10-92.

.2	"k" Value:  maximum 0.035 W/m.°C at 24°C mean temperature.

.3	Service Temperature:  -14°C to 100°C.

.4	Jacket:  factory applied vapour barrier jacket to CGSB 51-GP-52Ma, Type 1.

.2	Cold Equipment Insulation - Curved Surfaces:

.1	Material:  mineral fibre blanket to CAN/CGSB-51.11-92.

.2	"k" Value:  maximum 0.035 W/m.°C at 24°C mean temperature.

.3	Service Temperature:  -14°C to 100°C.

.4	Jacket:  factory applied vapour barrier jacket to CGSB 51-GP-52Ma, Type 1.

2.6	ACCESSORIES

.1	For mineral fibre insulation materials:

.1	FSK Tape: vapour barrier tape consisting of laminated aluminum foil, glass fiber scrim and paper, with pressure sensitive self adhesive.

.2	ASJ Tape: vapour resistant tape consisting of all service jacket material with pressure sensitive self adhesive.

.3	Adhesive:  quick setting adhesive for joints and lap sealing.

.2	Black Rubber Insulation Adhesive:  manufacturers recommended contact cement.

.3	Finishing Cement:  to CAN/CGSB-51.12-95 Type 1 - mineral fibre hydraulic setting thermal insulating and finishing cement for use up to 650°C.

.4	Insulating Cement:  to CAN/CGSB-51.12-95, Type 2 - mineral fibre thermal insulating cement for use up to 870°C.

SPEC NOTE:  CAN/CGSB-51.12-95 allows for three types of insulating and finishing cements as follows:

Type 1:	Mineral fibre hydraulic setting thermal insulating and finishing cement for use up to 650°C.

Type 2:	Mineral fibre thermal insulating cement for use up to 870°C.

Type 3:	Expanded or exfoliated vermiculite thermal insulating cement for use up to 980°C.

2.7	RECOVERY MATERIALS

.1	Canvas:  ULC listed, 220 g/m2  plain weave cotton fabric.

.2	Aluminum:  to 0.5 mm thick with longitudinal slip joints and 50 mm end laps, 0.4 mm thick die shaped fitting covers with factory attached protective liner on interior surface.

.3	PVC:  to CAN/CGSB-51.53-95, [0.38] [     ] mm thick for interior use [and [     ] mm thick for exterior use], off-white in colour with one-piece premoulded fitting covers.

.4	Black Rubber Finish:  insulation manufacturers recommended vinyl lacquer type coating.

3.	Execution

3.1	INSTALLATION, GENERAL

.1	Apply insulation after required piping system tests have been completed and inspected by the Minister.

.2	Ensure insulation is continuous through walls and floor penetrations.

.3	Ensure piping surface is clean and dry before insulating.

.4	Locate cover seams in least visible locations.

.5	Stagger butt joints where multi-layered insulation is used.

.6	On vertical piping with diameters 25 mm and larger, use insulation supports welded or bolted to pipe directly above lowest pipe fitting.  Repeat supports on 4.5 m centers and at each valve and flange.

.7	Tightly fit insulation sections to pipe to make smooth and even surfaces.  Cut insulation for proper fit where weld beads protrude.  Bevel away from studs and nuts to allow their removal without damage to insulation.  Trim closely and neatly around extending parts of pipe saddles, supports, hangers, clamp guides and seal with insulating/finishing cement.

3.2	HOT PIPE INSULATION APPLICATION

.1	Apply mineral fibre insulation when pipe surface temperatures are 50°C to 60°C.

.2	Apply mineral fibre insulation and recovery over full length of pipe without penetration of hangers, interruption at sleeves and fittings.  Seal butt joints with 100 mm wide ASJ tape.

.3	Terminate mineral fibre insulation at each end of unions and flanges.  Trowel finishing cement into bevel.

.4	Cover fittings and valves with equivalent thickness of finishing cement.  Apply finishing cement over exposed fittings and valves before applying canvas recovering.

.5	Cut mineral fibre insulation layers straight on 10 m centers with 25 mm gap to allow for expansion between terminations.  Pack void tightly with insulation and protect joints with aluminum sleeves.

.6	Seal black rubber insulation butt joints and seams with black rubber insulation adhesive.

.7	Recover exposed mineral fibre insulated piping with [canvas] [PVC] [aluminum].

.8	Recover mineral fibre insulated piping exposed to outdoors with aluminum.

.9	Coat exposed black rubber insulation with two coats of black rubber finish material.

.10	Do not insulate the following piping system components:

.1	Hot water heating piping in radiation cabinets.

.2	Unions, flanges, strainers, expansion joints, flexible piping connectors.

.3	Condensate trap assemblies and drip legs.

.4	Chrome plated or stainless steel piping.

.5	Valve bonnets on domestic water systems.

3.3	HOT EQUIPMENT INSULATION APPLICATION

.1	Use rigid fibreboard for flat surfaces and blanket for curved surfaces.

.2	Tightly butt edges and stagger joints.  Weld mechanical fastener pins to equipment where necessary.

.3	Cover insulation with 25 mm galvanized hexagonal mesh and 12 mm coat of insulating cement.  Finish with a final 12 mm coat of finishing cement and recover with canvas.

3.4	ENGINE EXHAUST INSULATION APPLICATION

.1	Ensure insulation is continuous through the wall or roof to point of termination.

.2	Cover elbows and fittings with equivalent thickness of insulating cement.

.3	Recover all piping, including muffler, with aluminum.

3.5	COLD PIPE INSULATION APPLICATION

.1	Insulate 2 m portion of plumbing vents measured from roof outlet back.  Do not insulate remaining vent piping.

.2	Insulate storm sewer piping throughout.  Insulate final 2 m portion from outlet drain back with 25 mm insulation.

.3	Apply mineral fibre insulation and recovery over full length of pipe without penetration of hangers, interruption at sleeves and fittings.  Apply adhesive to ends of butt joints and seal joint seams with 100 mm wide strips of joint tape.

.4	Insulate complete system including valves, unions, flanges, strainers.  Cover fittings and valves with equivalent thickness of finishing cement.  Cover finishing cement with open mesh glass cloth and adhesive.  Seal lap joints with 100% coverage of joint tape and seal the assembly with adhesive.

.5	Seal black rubber insulation butt joints and seams with black rubber insulation adhesive.

.6	Recover exposed mineral fibre insulated piping with [canvas] [PVC] [aluminum].

.7	Recover mineral fibre insulated piping exposed to outdoors with [aluminum] [PVC].

.8	Coat exposed black rubber insulation with two coats of black rubber finish material.

3.6	COLD EQUIPMENT INSULATION APPLICATION

.1	Tightly butt edges and stagger joints.  Seal joints with 100 mm wide FSK tape.

.2	Cover insulation with 25 mm galvanized hexagonal mesh and 12 mm coat of finishing cement.  Finish with a final 12 mm coat of finishing cement and recover with canvas.

3.7	INSULATION TYPE AND THICKNESS SCHEDULE

| Service Type and Nominal Pipe Diameter (mm) |  | Insulation Type | Insulation Thickness (mm) |
| --- | --- | --- | --- |
| Hot water heating |  |  |  |
|  | 50 and smaller | Hot pipe | 25 |
|  | 65 and larger | Hot pipe | 40 |
| Glycol heating |  |  |  |
|  | 50 and smaller | Hot pipe | 25 |
|  | 65 and larger | Hot pipe | 40 |
| Low pressure steam |  |  |  |
|  | 50 and smaller | Hot pipe | 40 |
|  | 65 and larger | Hot pipe | 50 |
| Condensate |  |  |  |
|  | 25 and smaller | Hot pipe | 25 |
|  | 30 to 50 | Hot pipe | 40 |
|  | 65 and larger | Hop pipe | 50 |
| Domestic hot water and recirculation |  |  |  |
|  | 40 and smaller | Hot pipe | 12 |
|  | 50 and larger | Hot pipe | 25 |
| Chilled water |  |  |  |
|  | 25 and less | Cold pipe | 12 |
|  | 30 to 50 | Cold pipe | 20 |
|  | 65 and larger | Cold pipe | 25 |

Continued next page

3.7	INSULATION TYPE AND THICKNESS SCHEDULE  (Cont'd)

| Service Type and Nominal Pipe Diameter (mm) |  | Insulation Type | Insulation Thickness (mm) |
| --- | --- | --- | --- |
| Refrigerant & Chilled glycol |  |  |  |
|  | 25 and smaller | Cold pipe | 25 |
|  | 30 and larger | Cold pipe | 40 |
| Domestic cold water |  |  |  |
|  | 40 and smaller | Cold pipe | 12 |
|  | 50 and larger | Cold pipe | 25 |
| Condenser water, |  |  |  |
|  | All sizes | Cold pipe | 25 |
| External sprayed coil |  |  |  |
|  | All sizes | Cold pipe | 12 |
| Condenser water piping indoors |  |  |  |
|  | 25 and smaller | Cold pipe | 25 |
|  | 30 and larger | Cold pipe | 40 |
| SPEC NOTE: Specify insulation for "Condenser water piping indoors" only when free cooling chillers or exchangers are specified. |  |  |  |
| Plumbing vents |  |  |  |
|  | All sizes | Cold pipe | 25 |
| Storm sewer piping, |  |  |  |
|  | All sizes | Cold pipe | 12 |
|  | Final 2 m section | Cold pipe | 25 |
| Emergency generator exhaust system |  |  |  |
|  | All sizes | Engine exhaust | 50 |
| Heat exchangers |  | Hot equipment | 50 |
| Hot water storage tanks |  | Hot equipment | 50 |

Continued next page

3.7	INSULATION TYPE AND THICKNESS SCHEDULE  (Cont'd)

| Service Type and Nominal Pipe Diameter (mm) |  | Insulation Type | Insulation Thickness (mm) |
| --- | --- | --- | --- |
| Condensate tanks |  | Hot equipment | 50 |
| Deaerators |  | Hot equipment | 50 |
| Heat exchangers |  | Cold equipment | 50 |
| Chillers |  | Cold equipment | 25 |
| Chilled water pumps |  | Cold equipment | 25 |
| Chilled water storage tanks |  | Cold equipment |  |
| Water softeners |  | Cold equipment | 25 |
| Condenser water storage tanks |  | Cold equipment | 25 |
| Roof drains |  | Cold equipment | 25 |

# END OF SECTION