Section Cover Page

Section 15123 2000-06-01 Tanks

This Master Specification Section contains:

.1	This Cover Sheet

.2	Data Sheet - Reference Standards

.3	Data Sheet - Product Selection and Specification

.4	Data Sheet - Design Notes

.5	Specification Section Text:

1.	General

1.1	Related Sections

1.2	Shop Drawings

1.3	Certificates

  - Detail Drawings

2.	Products

2.1	Pressure Vessels

2.2	Expansion Tanks - Pneumatic Vessel

2.3	Expansion Tanks - Bladder Type

2.4	Glycol Fill Tanks - Pressure Vessel Type

2.5	Glycol Fill Tanks - Atmospheric Vessel Type

2.6	Domestic Hot Water Storage Tanks

2.7	Underground Fuel Storage Tanks - Steel

2.8	Underground Fuel Storage Tanks - FRP

2.9	Aboveground Fuel Storage Tanks - Inside Building

  - Aboveground Fuel Storage Tanks - Outside Building

3.	Execution

3.1	Expansion Tanks - Pneumatic Vessel

3.2	Glycol Fill Tanks

3.3	Domestic Hot Water Storage Tanks

3.4	Underground Fuel Storage Tanks

3.5	Aboveground Fuel Storage Tanks - Inside Building

3.6	Tank Schedule

.6	Detail Drawings:

15123.01   Expansion Tank - Pneumatic Vessel

15123.02   Glycol Fill Tank Pressure Vessel Type

15123.03   Domestic Hot Water Storage Tank

15123.05   Underground Fuel Storage Tank Fill Assembly

Applicable Standards:

.1	CAN/ULC-S602-1992	Aboveground Tanks for Fuel Oil and Lubricating Oil

.2	CAN/ULC-S603-1992	Steel Underground Tanks for Flammable and Combustible Liquids

.3	CAN/ULCS603.1-1992	Galvanic Corrosion Protection System for Steel Underground Tanks

.4	CAN4-S615-1983	Reinforced Plastic Underground Tanks for Petroleum Products

Association and Institute Publications:

.1	ASME Boiler and Pressure Vessel Code, for Unfired Pressure Vessels.

* Documents referenced in the Specification text.

These reference documents may be available for reference purposes in the Technical Resources and Standards Branch Library, Alberta Infrastructure, 3rd Floor, 6950 - 113 Street, Edmonton; Telephone:  (780) 427-7924.

Determine which types of tanks are applicable to project.

Make a choice between bladder type expansion tanks and pneumatic vessel type expansion tanks.  Do not specify both.

Select domestic hot water storage tank where tanks are remote from heaters or heat exchanger.

Make a choice between ferrous and non-ferrous underground fuel storage tanks.  Do not specify both.

Refer to details that form part of this Section.  Ensure drawings and piping schematics are consistent with these details.  Use only those details that are applicable.

Refer to ASME Code for Unfired Pressure Vessels or to tank manufacturer's specific data for additional information.

Tanks used for the following systems must not be galvanized or coated with a zinc rich coating:

.1	Domestic Hot Water Systems

.2	Hot Water Heating Systems

.3	Glycol Systems

The zinc depletes the corrosion inhibitor resulting in accelerated corrosion in the system.

Pressurized Expansion Tanks for Glycol Systems, use the following types of tanks:

.1	Small Cooling Systems: standard or bladder type tank.

.2	Large Cooling Systems: bladder type tank.

.3	All Heating Systems: bladder type tank.

Glycol Charging tank requires:

.1	Air pressure reducing station.

.2	Adjustable pressure regulator.

.3	Isolating valves.

.4	Strainers.

.5	Check valves.

.6	Must not be connected to domestic water system.

END OF DATA SHEETS

1.	General

1.1	RELATED SECTIONS

.1	Earthwork: 	Division 2.

.2	Mechanical General Requirements:	Section 15010.

.3	Chemical Treatment and Cleaning - General Requirements:	Section 15184.

1.2	SHOP DRAWINGS

.1	Comply with requirements of Section 15010.

.2	Provide tank mounting details and special backfill requirements for buried tanks.

1.3	CERTIFICATES

.1	Submit inspection certificate for tanks that require inspection under the Alberta Safety Codes Act, Design, Construction and Installation of Boilers and Pressure Vessels Regulations.

1.4	DETAIL DRAWINGS

.1	Following detail drawings are appended hereto and form part of this Section.

No.	Name

15123.01	Expansion Tank - Pneumatic Vessel

15123.02	Glycol Fill Tank - Pressure Vessel Type

15123.04	Domestic Hot Water Storage Tank

15123.05	Underground Fuel Storage Tank Fill Assembly

2.	Products

2.1	PRESSURE VESSELS

.1	Fabricate pressure vessels to ASME Code for Unfired Pressure Vessels.

2.2	EXPANSION TANKS - PNEUMATIC VESSEL

.1	Body Construction:  closed type pressure vessel, welded steel.

.2	Coating:  red zinc rich primer outside only.

.3	Support:  steel saddles.

.4	Gauge Glass:  maximum 600 mm long section extended from top of tank to bottom; try cocks with ball check and guards.

.5	Accessories:

.1	Pressure gauge.

.2	Reduced pressure backflow preventer assembly.

.3	Pressure reducing valve.

.4	Relief valve.

.5	Quick connect air inlet.

.6	Air escape tank fitting.

.7	Sight glass assembly.

.8	Water make-up meter.

.9	Pressure regulator bypass.

.6	Tappings:  inlet, drain, pressure relief valve, gauge glass, pressure gauge, compressed air inlet.

2.3	EXPANSION TANKS - BLADDER TYPE

.1	Body Construction:  steel pressure vessel outer tank.

.2	Support:  steel skirt for vertical floor support.

.3	Air Chamber:  heavy duty butyl diaphragm bonded with polypropylene liner to steel shell, separating air chamber from water.  Chamber precharged to insure that a positive pressure of at least 35 kPa gauge is maintained at top of the system.

.4	Fittings:  air side charge connection; water side inlet connection.

2.4	GLYCOL FILL TANKS - PRESSURE VESSEL TYPE

SPEC NOTE:  Choose pressure vessel type or atmospheric type - not both.  Use pressure vessel type on larger projects.

.1	Body Construction:  closed type pressure vessel, welded steel.

.2	Coating:  red zinc rich primer, outside only.

.3	Support:  steel skirt for vertical floor support.

.4	Gauge Glass:  maximum 600 mm long sections from top of tank to bottom, brass try cocks, ball checks stops and guards.

.5	Accessories:

.1	Pressure Gauge.

.2	Funnel with valve on top of tank.

.3	Pressure reducing valve with bypass.

.4	Gauge glass assembly.

.6	Tappings:  inlet, discharge, drain, gauge glass, pressure relief valve.

2.5	GLYCOL FILL TANKS - ATMOSPHERIC VESSEL TYPE

.1	Body Construction:  welded steel, atmospheric vessel.

.2	Coating:  red zinc rich primer, outside only.

.3	Accessories:  portable type manual gear pump.

2.6	DOMESTIC HOT WATER STORAGE TANKS

.1	Body Construction:  closed type pressure vessel, welded steel.

.2	Coating:  red zinc rich primer, inside and out.

.3	Support:  steel support saddles.

.4	Lining:  minimum 20 mm thick internal corrosive resistant concrete lining.  Line tank and connections.

.5	Accessories:

.1	Thermometer:  as specified in Section 15130.

.2	Access manhole.

.3	Chlorine resistant stainless steel screwed fittings.

.6	Tappings:  inlet, outlet, drain pressure relief valve, water make-up, spare.

2.7	UNDERGROUND FUEL STORAGE TANKS - STEEL

.1	Body Construction:  atmospheric, welded steel tanks to CAN/ULC-S603-1992.

.2	Coating:  coal tar epoxy paint, minimum 0.4 mm dry film thickness.

.3	Support:  factory manufactured anchor straps coated with coal tar epoxy minimum 0.1 mm dry film thickness.  Anchor straps with neoprene isolating pads to avoid contact with tank.

.4	Accessories:  100 mm brass watertight cap and lock fill assembly, lifting lugs.

.5	Access:  500 mm diameter manhole into top of tank with waterproof lockable cover, gasket and dielectric telescoping sleeve.

.6	Fill Line:  anti-siphon supply connection with aluminum drop tube extended to bottom of tank, galvanized fittings.

.7	Vent Line:  galvanized tee and elbow assembly with 6 mm square mesh screen over fitting.

.8	Corrosion Protection:  to CAN/ULC-S603.1-1992.  Factory attach high purity zinc plate anode protection.  Provide CuSO4 test cell and portable meter.  Provide anodes as follows:

.1	One 4 kg anode for tanks 5000 L and less.

OR

.1	Two 4 kg anodes for tanks from 5000 L to 15,000 L.

OR

.1	Two 7.5 kg anodes for tanks 15,000 L to 35,000 L.

OR

.1	Three 10 kg anodes for tanks 35,000 L to 75,000 L.

OR

.1	Four 15 kg anodes for tanks 75,000 L to 125,000 L.

OR

.1	Six 20 kg anodes for tanks 125,000 L to 250,000 L.

.2	Two 7.5 kg anodes separately packaged for supply and return piping protection.

.9	Level Gauge:  wood tank gauging stick, manufacturer's standard.

.10	Tappings:  combination fill/suction, vent, return; each fitting with nylon insulating bushing.

2.8	UNDERGROUND FUEL STORAGE TANKS - FRP

.1	Body Construction:  atmospheric pressure type, fibreglass reinforced plastic to CAN4-S615-1983 complete with hemispherical ends as an integral part of tank without joints or seams.

.2	Support:  tie rods and hold down straps to concrete base, coated with asphalt based paint, minimum 0.1 mm dry film thickness.

.3	Accessories:  100 mm brass watertight cap and lock fill assembly.

.4	Access:  500 mm diameter manhole into top of tank with waterproof cover, gasket and fibreglass sleeve.

.5	Fill Line:  anti-siphon supply connection with aluminum drop tube extended to bottom of tank, galvanized fittings.

.6	Vent Line:  galvanized tee and elbow assembly with 6 mm square mesh screen over fitting.

.7	Level Gauge:  wood tank gauging stick, manufacturer's standard.

.8	Tappings:  combination fill/suction, vent, return.

2.9	ABOVEGROUND FUEL STORAGE TANKS - INSIDE BUILDING

.1	Body Construction:  atmospheric pressure type, welded steel construction, to CAN/ULC-S602-1992.

.2	Coating:  red zinc rich primer, inside and out.

.3	Support:  steel saddles.

.4	Gauge Glass:  maximum 600 mm long sections extending from top of tank to bottom, brass compression stops and guards.

.5	Tappings:  vent, overflow return, inlet, outlet, level control, gauge glass, drain.

2.10	ABOVEGROUND FUEL STORAGE TANKS - OUTSIDE BUILDING

.1	Body Construction:  atmospheric pressure type, welded steel construction.

.2	Coating:  prime coat inside and out, aluminum finish coat.

.3	Support:  [skids] [2100 mm elevated stand] with primer coat and aluminum finish coat.

.4	Accessories:  vented locking fill cap.

.5	Tappings:  standard pipe thread welding flanges, fill/vent, outlet.

3.	Execution

3.1	EXPANSION TANKS - PNEUMATIC VESSEL

.1	Refer to Detail 15123.01.

.2	Provide pressure relief valve and pipe discharge to drain.  Set relief valve for tank rated pressure specified in schedule.

.3	Provide automatic water fill assembly with pressure reducing valve; reduced pressure backflow preventer assembly with shut-off valves, test cocks and vacuum breaker; water meter with valved bypass.

.4	Connect expansion line at bottom of tank with factory supplied air escape tank fitting.

.5	Provide quick connect air inlet of automotive tire valve type.  Extend inlet to accessible from floor level.

.6	Provide valved tank drain; pipe to floor drain.

.7	Support tank on metal frame mounted on floor where necessary

3.2	GLYCOL FILL TANKS

.1	Refer to Detail 15123.02.

.2	Provide pressure relief valve and pipe discharge to drain.  Set relief valve for tank rated pressure listed in schedule.

.3	Provide pressure gauge air supply to tank.

.4	Provide quick connect air inlet of automotive tire valve type.

.5	Provide valved tank drain; pipe to floor drain.

.6	Provide pressure reducing valve assembly on glycol discharge to system.

.7	Mount tank on floor.  Allow accessible work space around tank.

3.3	DOMESTIC HOT WATER STORAGE TANKS

.1	Refer to Detail 15123.03.

.2	Provide pressure relief valve; pipe discharge to drain.  Set relief valve for tank rated pressure specified in schedule.

.3	Provide thermometer on inlet and discharge pipes.

.4	Provide valved tank drain; pipe to floor drain.

.5	Support tank on steel saddle directly to floor.

3.4	UNDERGROUND FUEL STORAGE TANKS

SPEC NOTE:  This Section does not presently include a standard detail drawing for underground fuel storage tanks.  Ensure that tanks are detailed on drawings or on a detail drawing added to Section.

.1	Refer to Detail 15123.05 for fill assembly.

.2	Install steel fuel tank and piping in accordance with CAN/ULC-S603-1992 and CAN/ULC-S603.1-1992 including Appendix 'B' and tank manufacturer's installation instructions.

OR

.2	Install FRP fuel tank in accordance with CAN4-S615-1983 including Appendix 'A' and tank manufacturer's installation instructions.

SPEC NOTE:  CAN/ULC-S603.1-1992 and CAN4-S615-1983 contain detailed requirements for installation of steel and FRP tanks.  Review these requirements and modify them as required to suit project.

.3	Notify Minister minimum of 24 hours prior to commencement of backfilling.

.4	Provide fuel for testing of tanks.

.5	After completion of testing, fill tanks with fuel specified in tank schedule.

3.5	ABOVEGROUND FUEL STORAGE TANKS - INSIDE BUILDING

.1	Support from building structure.

.2	Elevate aboveground fuel storage tanks to provide a positive head at the engine.

.3	Provide fuel for testing of tanks.

.4	After completion of testing, fill tanks with fuel specified in tank schedule.

3.6	TANK SCHEDULE

|  | Tank Designation |  |  |
| --- | --- | --- | --- |
|  | TK-[ ] | TK-[ ] | TK-[ ] |
| Location |  |  |  |
| Service |  |  |  |
| Capacity L |  |  |  |
| Diameter mm |  |  |  |
| Overall length mm |  |  |  |
| Rated pressure kPa |  |  |  |
| Working pressure kPa |  |  |  |
| Remarks |  |  |  |

SPEC NOTE:  For service identify fluid contained in tank.

SPEC NOTE:  Include Tank Schedule in this Section, not on drawings.

# END OF SECTION