Section Cover Page

Section 15906 2000-06-01 Control Systems

Use this Section to specify pneumatic, electric and electronic controls systems where the project size and complexity do not warrant use of a digital energy management and control system.

Refer to Section 15910 for requirements for Energy Management and Control Systems (EMCS).

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Quality Assurance

  - Submittals

2.	Products

2.1	General

2.2	Air Compressor and Receiver

2.3	Air Piping

2.4	Thermostats

2.5	Humidistats

2.6	Control Valves

2.7	Dampers

2.8	Damper Operators

2.9	Time Clocks

2.10	Alarm System

  - Control Panels

3.	Execution

3.1	Installation

3.2	Alarms

3.3	Heating Water Control

3.4	Combustion Air Unit Heaters

3.5	Cabinet and Unit Headers

3.6	Radiation

3.7	Reheat Coil

3.8	Terminal High Velocity Units

3.9	Induction Units

3.10	Fan Coil Units

3.11	Ventilation System

3.12	Central Refrigeration System

3.13	Excess Pressure Control

3.14	Elevator Machine Room

3.15	Electrical Rooms and Telephone Rooms

3.16	Emergency Generator Ventilation

3.17	Humidifier Control

3.18	Refrigeration System Control

3.19	Parkade Ventilation System

3.20	Smoke Ventilation

3.21	Gas Fired Unit Heater

1.	General

1.1	QUALITY ASSURANCE

.1	Provide complete system of automatic controls for mechanical systems supplied and installed by firms specializing in this type of work.

.2	At completion of installation provide minimum of [     ] days instruction period for operating personnel.

.3	Provide for complete service of controls systems, including call-backs, for one year running concurrent with guarantee.  Make minimum of [     ] complete inspection of approximately [     ] hours duration in addition to normal service calls to adjust controls with reports written and submitted to the Minister.

1.2	SUBMITTALS

.1	Provide damper shop drawings which include data such as arrangement, velocities and static pressure drops for each system on shop drawings.

.2	Provide shop drawings including complete operating data, system drawings, wiring diagrams and written detailed operational description of sequences, and description and engineering data on each control system component.  Include sizing as requested.

.3	At completion of work, make detailed checkout of automatic control system and submit written report to the Minister.

.4	Provide control diagrams for each system, framed under glass for wall mounting.

2.	Products

2.1	GENERAL

.1	Provide control systems consisting of thermostats, control valves, dampers, operators, indicating devices, interface equipment and other apparatus required to operate mechanical system and to perform functions specified.

.2	Provide the necessary components to connect factory supplied controls with certain equipment where such controls are specified.

.3	Unless specified otherwise, provide fully proportional components.

2.2	AIR COMPRESSOR AND RECEIVER

.1	Provide [simplex] [duplex] belt driven air compressor and tank unit complete with belt guard, silencers, flexible connections, air cleaner, automatic and manual drain assemblies, oil and particle filler (0.5 micrometre) and pressure reducing and pressure relief valves.

.2	Combination size of compressor and storage tank shall limit compressor starts at 10 maximum per hour and 50% running time.

.3	Provide electrical alternation set to operate each compressor [alternately] [12 hours] with provision for second compressor to cut in on demand.  Cycle compressors through pressure switch.  If one compressor fails other automatically maintains air pressure.

.4	Provide refrigerated, non-cycling, air dryer, complete with automatic drain trap assembly and capacity to lower dew point to 15°C to 140 kPa.  Mount unit in discharge air line from tank.

2.3	AIR PIPING

.1	Piping, Type "K" hard or soft drawn copper or polyethylene plastic tubing.

.2	Use copper lines in mechanical rooms, where subject to damage or temperatures in excess of 90°C, where adjacent to heating pipes passing through common sleeve and where not readily accessible.  In mechanical room, bundled plastic tubing with suitable junction boxes or single plastic tubing with tray may be used.

.3	Leave two spares and pair of communication lines in bundled plastic tubing.

.4	Run exposed piping only in storage or similar type rooms.

.5	Install pressure gauges on branch lines, at each controller and at each actuator and relay.

.6	Provide air lines, checks and hand valves to expansion tanks with tank fitting and hand valve.

2.4	THERMOSTATS

.1	Provide room thermostats with celsius scale, single temperature, gradual-acting, adjustable sensitivity.  Provide covers with [exposed] [concealed] set point adjustment, set point indication and [with] [without] thermometer.  Provide guards for thermostats in unsupervised or public areas.  Range 10°C - 35°C with maximum of 1°C set point adjustment.

.2	Freeze protection thermostats shall be manual reset type with 6.1 m element located to ensure maximum protection.  Provide multiple thermostats for large duct cross sectional areas.

.3	Remote bulb elements shall be either averaging type of suitable length for air or rigid bulb type for liquids.  Use stainless steel flanges to support elements in ducts.  In liquids, use separable wells.

2.5	HUMIDISTATS

.1	Humidity controllers shall be direct or reverse acting with differential not exceeding 5% relative humidity with minimum 60% set point adjustment.

2.6	CONTROL VALVES

.1	Provide valves in accordance with general valve specification.  Provide position indicators on valves and pilot positioners on sequenced valves.

.2	Valves shall "fail safe" in normally open or closed position as dictated by freeze, humidity, fire or temperature protection.

.3	Two-way valves for liquids shall have equal percentage characteristics.  Three way valves shall have linear characteristics.  Size valve operators to close valves against pump shut off head.  Size for maximum 20 kPa drop.

.4	Steam valves shall have modified linear characteristics with stainless steel seats.  Provide separate valves on individual coils.  Capacities for two valves in parallel shall have 1/3 - 2/3 load capacities sequenced so that smaller valve opens first.  Size low pressure valves for approximately 70 kPa inlet pressure and 35 kPa drop.

2.7	DAMPERS

.1	Automatic dampers shall be 1.6 mm galvanized steel or extruded aluminum multiple blade mounted in 3.0 mm steel or extruded aluminum flanged frame.  Individual blades shall not exceed 150 mm in width or 1200 mm in length with interlocking edges and compressible seals.  Provide oil impregnated bronze or nylon bearings with additional thrust bearings for vertical blades.  Prime coat steel dampers.

.2	Mixing dampers of [opposed] [parallel] blade construction arranged to mix air stream.  Provide positive positioning on mixed air dampers where dampers are not mechanically linked.  Provide separate minimum outside air damper section adjacent to return air dampers with separate damper motor.  Dampers, maximum 1% leakage.

2.8	DAMPER OPERATORS

.1	Piston or gear driven type damper operators with spring return to "fail safe" in normally closed position as dictated by freeze, fire or temperature protection.  Provide pilot positioners on operators sequenced with other controls.

.2	Provide one damper motor for approximately 4 m2 damper section [or minimum of one damper motor per damper section.]

2.9	TIME CLOCKS

.1	Provide seven day programming clocks with power failure spring carry over good for 10 hours and multiple contacts as required to control systems for minimum two signals every 24 hours.

.2	Provide multi-pole relays compatible with controlled devices to sequence operation.

.3	Provide manual override switches.  Include time delays devices for major electrical loads.

2.10	ALARM SYSTEM

.1	Provide alarm panel with individual indication, horn, silencing and acknowledge switch and test switch.  At any alarm condition indication light will come on and alarm will sound.  Depressing acknowledge button shall stop horn.  Should second alarm occur before first one corrected, alarm shall again sound.

.2	Provide remote panels in locations shown with indication activated by any alarm, silencing and acknowledge switch and test switch.  Interlock silencing and acknowledge switch.

.3	Provide duplicate panels in locations shown to serve functions of primary panel.  Interlock silencing and acknowledge switch.

.4	Provide an additional set of contacts suitable for connecting alarm panel and signalling outside independent alarm monitoring company.

2.11	CONTROL PANELS

.1	Provide local panels of unitized cabinet type for each system under automatic control.  Mount relays, switches, and controllers with control point adjustment in cabinet and temperature indicators, pressure gauges, pilot lights, push buttons, and clocks and switches flush on cabinet panel face.

.2	Fabricate panels from 3.0 mm furniture steel with baked enamel finish and hinged key lock door.

.3	Mount panels adjacent to associated equipment on vibration free walls or free standing angle iron supports.  One cabinet may accommodate more than one system in same equipment room.  Provide engraved plastic name plates for instruments and controls inside cabinet and on cabinet face.

3.	Execution

3.1	INSTALLATION

.1	Check and verify location of thermostats and other exposed control sensors with plans and room details before installation.  Locate thermostats 1.5 m above floor.

.2	Install damper motors on outside of ducts.  Do not locate in outside air stream.

3.2	ALARMS

.1	Provide alarm points complete with all equipment necessary for remote signalling to alarm panel for the following conditions:

-	No water (glycol flow)

-	Low air temperature

-	Low control pressure

-	Controls compressor failure

-	Sump pumps (high level)

-	Boiler failure (common point for multiple boilers)

-	Low heating water (glycol) temperature

-	Cooling tower freeze (dump)

-	Low pressure

-	Condensate tank (high and low levels)

-	Low humidity

-	High humidity

-	Expansion tank (low level)

-	No flow air systems (air heating systems)

-	Off normal temperature

-	Equipment operation [fan] [pumps] [emergency generators] [fire pump].

.2	Interlock alarms with starter switching to bypass alarm when equipment is manually disconnected.

3.3	HEATING WATER CONTROL

.1	Provide flow switches in each pump discharge to provide on-off indication.

.2	Outdoor sensor shall reset a discharge water sensor and controller [to modulate the steam control valves] [to modulate the primary water control valve] [to modulate the boilers gas valve] [to step fire the boilers].

.3	Provide flow switch in pump circuit to [close control valve on no flow conditions and] indicate alarm.  Provide alarm bypass switch.

.4	Provide on local control panel:

-	System graphic

-	System supply temperature

-	System supply control point adjustment

-	System return temperature

-	Pump on-off switch

-	Pump on-off indication

-	Boilers lead-lag switch

3.4	COMBUSTION AIR UNIT HEATERS

.1	Thermostat shall modulate [2-way] [3-way] heating control valve.  Aquastat on return heating water line shall stop unit on low temperature.

3.5	CABINET AND UNIT HEATERS

.1	Electric thermostats shall cycle unit motor.  [Aquastat on return heating water line from flow mounted cabinet heaters shall stop unit on low temperature.

3.6	RADIATION

.1	Thermostat shall modulate 2-way heating control valve.

3.7	REHEAT COIL

.1	Thermostat shall modulate 2-way heating control valve.

3.8	TERMINAL HIGH VELOCITY UNITS

.1	Thermostat shall modulate 2-way heating control valve.

.2	Thermostat shall modulate [variable volume damper operator] [and] [dual duct damper operator.  [Where reheat coils or radiation is also provided, sequence 2-way heating control valve with damper operator.]

3.9	INDUCTION UNITS

.1	Unit mounted thermostats shall modulate 2-way induction control valve.

3.10	FAN COIL UNITS

.1	Thermostat shall modulate 2-way heating control valve and 2-way cooling control valve in sequence.

.2	Mount thermostat with adjustable knob and speed switch on common plate engraved with "Heating Control and Fan Control" at top, "Warmer and Cooler" and direction around thermostat knob, and fan speeds, to approval of the Minister.

3.11	VENTILATION SYSTEM

.1	Fully open preheat coil valve to heating if outside air temperature is below 5°C [whether fan is running or not] [when fan is not running].

.2	Supply air to controls when supply fan is started [and open outside air damper.

.3	Provide freezestat [before supply fan] [downstream of preheat coil] [and aquastat freeze protection in preheat coil return line] to stop supply fan [and close outside air dampers.

.4	Provide damper end switch to prevent supply fan starting until damper is open.

.5	Return air humidistat reset from outdoors shall [modulate normally closed humidifier valve] [cycle spray pumps and modulate valve on spray header.  Interlock spray pumps with supply fans and sump low level control.  Set outdoor reset to 50% R.H. at 21°C and 15% R.H. at -37°C.

.6	Thermostat in mixed air shall modulate [mixed air dampers] [preheat coil valve] [and face and bypass dampers] [in sequence].

.7	Thermostat in supply air duct shall modulate mixed air dampers [preheat coil valve] [and face and bypass dampers] [and cooling coil valve] in sequence.

.8	Outside air thermostat above [    ]°C shall close outside air damper [to minimum position] [leaving minimum outside air damper open.

[Interlock return fan to start with supply fan.]

[Interlock supply fan to start when exhaust fan is started]

[Interlock exhaust fan to start with supply fan.]

[Return fan shall run continuously.]

.10	Each zone thermostat shall modulate its zone mixing dampers.  [Modulate reheat coil valve through selective relay by zone thermostat calling for greatest heating.  [Similarly zone thermostat calling for greatest cooling shall modulate cooling coil valve.]

.11	Outdoor thermostat shall reset hot deck thermostat to modulate reheat coil valve.  [Cold deck thermostat shall modulate cooling coil valve to maintain constant temperature.]

.12	Outdoor thermostat shall reset induction system [zone] supply thermostat to modulate reheat coil valve.

.13	Pressure sensor shall modulate supply and return fan inlet vane dampers in sequence to maintain constant static pressure.  Locate sensor minimum 15 m downstream of supply fan in supply air duct.

.14	Pressure sensor shall modulate supply fan inlet vane dampers to maintain constant supply static pressure.  Modulate return air fan inlet vane dampers to maintain constant building pressurization.

.15	Pressure sensor shall modulate supply fan inlet vane dampers to maintain constant supply static pressure.  Modulate return fan inlet vane dampers from velocity pressure measurements in supply and return ducts to maintain constant differential air flow rate.

.16	Provide time clock for day-night control with manual bypass switch marked "Day-Auto-Night".  [On night cycle close outside air dampers].  [Below 10°C on night cycle pumps shall be stopped, outside air dampers closed and fans shall continue to run].

.17	Provide on local control panel:

-	System graphic

-	System on-off-auto switch

-	System on-off indication

-	System day-night-auto switch

-	Supply fan on-off-auto switch

-	Supply fan on-off indication

-	Return fan on-off [auto] switch

-	Return fan on-off indication

-	Preheat coil pump on-off switch

-	Preheat coil pump on-off indication

-	Spray pump on-off-auto switch

-	Spray pump on-off-auto indication

-	Outside air temperature indication

-	Mixed air temperature indication

-	Fan discharge air temperature indication

-	Reheat zone air temperature indication

-	Return humidity indication

-	Fan discharge temperature control point adjustment

-	Return humidity control point adjustment

-	Reheat zone control point adjustment

-	Supply static pressure indication

-	Supply static pressure control point adjustment

3.12	CENTRAL REFRIGERATION SYSTEM

.1	Interlock condensing water pump with level control in cooling tower.  Interlock chilled water pump and cooling tower fans to start when condensing water pump started.  [When chilled water pump starts chiller control valve shall open.  Modulate chiller control valve to maintain constant pressure differential.

.2	When chilled water flow and condensing water flow is proven by flow switches, refrigeration machine shall be allowed to start automatically initiate condensing water pump start from refrigeration machine.  Pumps shall not operate, automatically, unless refrigeration machine is operating.

.3	Thermostat in condenser water line shall cycle cooling tower fans to maintain [13] [24] [    ]°C minimum condenser water.

.4	Thermostat in cooling tower sump shall cycle electric sump heaters to maintain 4.5°C sump temperatures.  Outdoor thermostat shall activate piping electric heat tapes.

.5	Thermostat in cooling tower sump, set for 1.5°C will open drain lines and close make-up valve, deactivate sump heaters and piping electric heat tapes.

.6	If outdoor temperature is above 10°C refrigeration system is allowed to start.

.7	Provide time clock with manual bypass switch marked "on-off-auto" to [start and] stop refrigeration system.

.8	Provide on local control panel:

-	System graphic

-	Condensing water pump on-off (auto) switch

-	Condensing water pump on-off indication

-	Chilled water pump on-off-auto switch

-	Chilled water pump on-off indication

-	Chiller on-off [auto] switch

-	Chiller on-off indication

-	Chiller condensing water supply and return temperature

-	Chiller water supply and return temperature

-	Chiller condensing water control point adjustment

-	Common chilled water supply temperature

-	Chilled water control point adjustment

-	Low level cooling tower sump

-	Expansion tank low level alarm

-	Cooling tower fan pilot lights

-	Cooling tower sump heater pilot lights

-	Cooling tower dump on-off switch

-	Cooling tower dump indication

3.13	EXCESS PRESSURE CONTROL

.1	[Open modulating bypass valve] [Cycle pumps in sequence] [Vary pump speed through variable drive control] from controller sensing pressure differential between supply and return lines].

3.14	ELEVATOR MACHINE ROOM

.1	On temperature rise, thermostat shall open intake dampers and start exhaust fans.

3.15	ELECTRICAL ROOMS AND TELEPHONE ROOMS

.1	On temperature rise, thermostat shall open intake damper and start exhaust fan.

3.16	EMERGENCY GENERATOR VENTILATION

.1	On temperature rise, thermostat shall modulate outside and exhaust dampers open, and recirculation dampers closed.

.2	On temperature rise, thermostat shall open intake damper and start exhaust fan.

.3	Provide solenoid valve to positively shut off fuel supply when generator is not operating.

3.17	HUMIDIFIER CONTROL

.1	Line voltage thermostat shall [cycle unit fan and] open 2-position, 2-way [steam] [hot water] valve.

3.18	REFRIGERATION SYSTEM CONTROL

.1	Thermostat located in [supply] [return] air duct shall cycle refrigeration system and step capacity minimum of [     ] steps.

.2	When refrigeration system is started return mixing dampers to minimum outdoor air position.

3.19	PARKADE VENTILATION SYSTEM

.1	Time clock shall stop parkade exhaust fan at night.

3.20	SMOKE VENTILATION

3.21	GAS FIRED UNIT HEATER

.1	Line voltage thermostat shall cycle gas valve and fan simultaneously to maintain set temperature.

.2	Fan[s] to be capable of independent operation for summer air circulation.

END OF SECTION