Section Cover Page

Section 02532 Sanitary Sewage 2000-03-22 Force Main System

Use this Section to specify requirements which apply specifically to sanitary sewage force main system.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Intent

1.2	Related Sections

1.3	Section Includes

1.4	Detail Drawings

1.5	Unit Prices

1.6	Testing by Contractor

2.	Products

2.1	Materials Schedule

2.2	Bedding Materials

3.	Execution

3.1	Force Main Installation

.3	Detail Drawing:

02532.01	Sewage Force Main Flushout

Applicable Standards:

.1	ANSI/AWWA C104/A21.4-95	Cement-Mortar Lining for Ductile-Iron Pipe and Fittings for Water

.2	ANSI/AWWA C110/A21.10-93	Ductile-Iron and Gray-Iron Fittings, 3 in through 48 in, (75mm through 1200 mm) for Water and Other Liquids,

.3	ANSI/AWWA C504-94	Rubber-Seated Butterfly Valves

.4	CGSB 41-GP-25M		Pipe, Polyethylene, for the Transport of Liquids

.5	CSA B137.1-95	Polyethylene Pipe, Tubing and Fittings for Cold Water Pressure Services

.6	CSA B137.3-93	Rigid Poly (Vinyl Chloride) (PVC) Pipe for Pressure Applications

These reference documents may be available for reference purposes in the Technical Resources and Standards Branch Library, Alberta Infrastructure, 3rd Floor, 6950 - 113 Street, Edmonton; Telephone:  (780) 427-7924.

1.	General

1.1	INTENT

.1	Read this Section in conjunction with Section 02501 - Piped Utility Systems General Requirements.

1.2	RELATED SECTIONS

.1	Trench Excavating & Backfilling:	Section 02319.

.2	Piped Utility Systems General Requirements:	Section 02501.

1.3	SECTION INCLUDES

.1	This Section includes all requirements for sanitary sewage force main, including materials, installation of pipes, appurtenances and testing of the completed system.

1.4	DETAIL DRAWINGS

.1	Following detail drawing is appended hereto and forms part of this Section:

02532.01	Sewage Force Main Flushout

SPEC NOTE:  Include detail drawing only if applicable to project.  Co-ordinate working drawing details with detail drawing.

1.5	UNIT PRICES

| Unit of Work Description | Unit of Measurement | Method of Measurement |
| --- | --- | --- |
| Pipe [and fittings] | m | Length installed, measured along pipe invert, through all fittings & appurtenances |
| SPEC NOTE: Delete following item if included in .1 above. |  |  |
| Pipe Fittings | Each | Number installed |
| Valves and Valve [boxes][chambers] | Each | Number installed |
| Pipe Bedding | [m][m3] [tonne] | [Length of trench measured along pipe invert][Volume of material installed, by truck measure] [By tonne weight] |
| Bedding stabilization including removal and disposal of un- suitable materials | [m3] [tonne] | [Volume of material installed by truck measure][By tonne weight] |

SPEC NOTE:  Include this article for Unit Price Contracts only.

1.6	TESTING BY CONTRACTOR

.1	Conduct test in presence of Minister and provide all equipment required for the test.

.2	Water required for the test will be supplied [by the Minister] [by the Contractor].

.3	Conduct test after concrete thrust blocks have completely cured (minimum 7 days for standard concrete and 2 days for high early strength concrete.)

.4	Leave joints, fittings, valves and accessories exposed for inspection by Minister.

.5	Ensure minimum disruption to existing system during testing.

.6	Supply gauges, measuring device for the leakage test, pump, pipe, connections and all other necessary apparatus required for the test.

SPEC NOTE:  Delete Item .7 for Polyethylene (PE) pipe

.7	Test Procedure:

.1	Slowly fill pipe with water ensuring all air is expelled from the line.

.2	Apply a hydrostatic pressure of 1 1/2 times the rated pressure of the pipe.

.3	Maintain test pressure for the duration of the test (1 hour).

.4	Visually examine all exposed pipe, fittings, valves and appurtenances for leakage.

.5	Leakage test will consist of measuring amount of water required to maintain test pressure for one hour.  Installation will be rejected if the leakage is greater than that determined by the formula:

L = ND (Square Root of P)

70 500

where L = allowable leakage in L/h

N = number of joints in length tested

D = nominal diameter of pipe in mm

P = average test pressure in kPa.

.6	Repair or replace defective elements and repeat the test until the allowable leakage requirement has been met.

.7	Prevent force main from freezing, during the test.

SPEC NOTE:  Use Item .8 only for polyethylene pipe.

.8	Conduct pressure and leakage test for polyethylene pipe, in accordance with the manufacturer's test procedures.

2.	Products

2.1	MATERIALS SCHEDULE

| Material | Standard | Type | Joints |
| --- | --- | --- | --- |
| PVC pipe | CSA B137.3-93 | SDR [32.5] [26] [21] [18] | [Rubber gasket bell end] |
| Polyethylene pipe (PE) | CSA B137.1-95 (150 mm and smaller CGSB 41-GP-25M (200 mm and larger) | Series [45] [60] [80] [100] [125] [160] | [Butt fused] [Mechanical] ] |
| Cast iron fittings and specials cement lined | ANSI/AWWA C110/A21.10-93 ANSI/AWWA C104/A21.4-95 | Pressure rated [0.862 MPa] [1.724 MPa] | [Mechanical] [Flanged] [ ] |
| Gate valves | ANSI/AWWA C110/A21.10-93 | [Non-rising spindle] [square nut] [control rod] [Open anti- clock-wise] | [Mechanical] [Flanged] [ ] |
| Butterfly valves | ANSI/AWWA C504-94 | [Hand wheel] [Gear] operated [ ] | [Mechanical] [Flanged] [ ] |

2.2	BEDDING MATERIALS

.1	Granular Material:  [Sand] [[   ] mm Crushed Gravel] as specified in Section 02056.

3.	Execution

3.1	BEDDING

.1	Provide Class [A] [B] [C] bedding as indicated on detail drawing appended to Section 02501.

3.2	FORCE MAIN INSTALLATION

.1	Install pipes, fittings, valves, so as to provide a fully functional system.

END OF SECTION