Section Cover Page


Section 07242


Class PM Exterior Insulation

1999-09-23
and Finish Systems

Use this Section to specify site applied Class PM (polymer modified, thick coat) exterior insulation and finish systems (EIFS).  Use Section 07261 - Sheet Membrane Air and Vapour Seal in conjunction with this Section, subject to coordination with EIFS manufacturer where noncombustible mineral wool insulation is specified.

Use Section 07241 - Class PB (polymer based, thin coat) Exterior Insulation and Finish Systems, to specify EIFS if this type of system has properties more suitable for the project.  Refer to System Selection criteria on Data Sheet - General.

This Master Specification Section contains:

.1
This Cover Sheet

.2
Data Sheet - General

.3
Data Sheet - Code Requirements

.4
Data Sheet - Design Considerations

.5
Data Sheet - Insulation and Appearance Requirements

.6
Specification Section Text:

1.
General

1.1
Section Includes

1.2
Related Sections

1.3
Reference Documents

1.4
Performance Requirements

1.5
Submittals

1.6
Certification

1.7
Applicator Qualifications

1.8
Regulatory Requirements

1.9
Mock-Up

1.10
Inspection By Minister

1.11
Delivery, Storage and Handling

3.9 Environmental Conditions

3 Coordination and Sequencing

2.
Products
3.9 [Combustible] Insulation

3 Noncombustible Insulation

2.3
Fastening Devices

2.4
Mesh Reinforcement

2.5
Base Coat

2.6
Finish Coat

2.7
Sealants

2.8
Accessories

3.
Execution
3.1
Examination and Preparation

3.2
Installation of Insulation  

3.3
Installation of Accessories

3.4
Mesh Installation

3.5
Base Coat Application

3.6
Finish Coat Application

3.7
Joint Sealant Application

3.8
Cleaning

3.9 Finish Coat Schedule

Applicable Standards

.1
ASTM A653M-96
Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot Dip Process

.2
CAN/CGSB-19.13-M87
Sealing Compound, One-Component, Elastomeric, Chemical Curing

.3
CAN/CGSB 51.10-92
Mineral Fibre Board Thermal Insulation

.4
CAN/CGSB 51.20-M87
Thermal Insulation, Polystyrene, Boards and Pipe Covering

.5
CAN/CSA-A5-93
Portland Cement

.6
CAN4-S114-80(R1985)
Determination of Non-Combustibility in Building Materials

These reference documents may be available for reference purposes in the Technical Resources and Standards Branch Library, Alberta Infrastructure, 3rd Floor, 6950 - 113 Street, Edmonton; Telephone: (780) 427-7924.

SYSTEM DESCRIPTION

Exterior Insulation and Finish Systems (EIFS) for Alberta Infrastructure projects consist of insulation covered by lamina made of base coat, reinforcement and finish coat.  Systems must be mechanically fastened to substrates.  EIFS are included in the Alberta Construction Tendering System (ACTS) trade definition for Lath, Plaster and Stucco. 

Master specifications for EIFS are available for Class PM (polymer modified, thick coat) and Class PB (polymer based, thin coat).  The two differ primarily in the method of installation of reinforcement and in base coat thickness.  With Class PM systems, mesh is mechanically anchored through insulation to structural substrates, prior to base coat application.  The mesh supports a 5 mm to 12.5 mm thick, polymer-modified and fibre-reinforced cementitious base coat.  Acrylic based finish coats are applied to both systems in various thicknesses, textures, patterns, and colours.

SYSTEM SELECTION
The environment into which EIFS is being placed should determine whether Class PM or Class PB is chosen.  Class PM systems are better than Class PB systems in withstanding penetration by sharp objects, such as the butt end of hockey sticks or broom handles, knives, and broken glass.  Class PB systems are more resistant to damage from impact by blunt objects.  Joint requirements for Class PM systems are similar to those of cement plaster.  Class PB systems require fewer joints. 

SYSTEM PERFORMANCE
EIFS provide thermal insulation and weather protection components of exterior walls, fascias and soffits.  Physical and performance characteristics have been established by the Exterior Insulation Manufacturers Association (EIMA) and the Association of Wall and Ceiling Contractors (AWCC).  Test methods for freeze-thaw stability, water vapour transmission, mildew resistance, weathering resistance, abrasion resistance, water absorption, impact resistance and negative wind load are referenced in the "Specification Manual for the Wall and Ceiling Industry".  This Manual is available from the Alberta Drywall, Lath and Plaster Association.  Noncombustible PM systems have been developed but are not available from all manufacturers. 

COORDINATION WITH DRAWINGS

Where more than one type of EIFS is used on a project, ensure drawings clearly indicate location and extent.  Ensure that terminology on drawings is consistent with specifications, e.g., drawings should only note "exterior insulation and finish system (EIFS)" and "rigid insulation".  Because of the potential for conflict with specifications, drawings should not indicate thicknesses or RSI values.

EIFS is typically a combustible cladding system limited in its application by code.  Noncombustible systems are available but, due to the height and floor area of most government facilities, are less frequently a code requirement.

The Alberta Building Code addresses the use of combustible cladding and protection of combustible insulation in the following: 

Subsection 3.1.5 - Noncombustible Construction - imposes height restrictions and testing requirements.

Subsection 3.2.3 - Spatial Separation and Exposure Protection of Buildings - contains prescriptive requirements or invokes requirements in Subsection 3.1.5.  

The Appendix to the 1990 Alberta Building Code, A-3.1.5.5.(1), states that the requirements for combustible cladding are based on the assumption that manufacturing and installation are carried out under an independent quality assurance program designed to confirm that product and application are consistent with system as tested.

Consult the current Alberta Building Code.  If there is uncertainty about interpretation of code requirements, consult with authority having jurisdiction.

DESIGN CONSIDERATIONS

Do not locate insulation in the building envelope which is additional to the insulation included in the EIFS.  

Make changes in plane, reveals and recesses as shallow as possible and curve or bevel transitions.  Avoid placing such features at stress locations.  Keep recesses to a minimum.

Provide minimum 1:2 slope to drain projections, sills, and bottoms of reveals and recesses.  Shallower slopes invite accumulations of water, snow, ice, bird excrement, and dirt, which usually lead to premature failure of the lamina.

Where EIFS is subject to abuse, consider a more durable material such as masonry, or provide surface joints to enable repairs to smaller, modular areas, with planned terminations.

Use bollards, curbs, landscaping or other suitable means to protect EIFS from vehicle traffic or occupant activities such as furniture moving.

EIFS AND THE RAIN SCREEN PRINCIPLE
Because of failures experienced with exposed seal systems such as conventional EIFS, Alberta Infrastructure requires a sheet membrane air and vapour seal between substrates and EIFS.  This will enable the application of the "rainscreen principle" to design of joint seals, and the entire system.  Specifiers are encouraged to evaluate and incorporate "rain screen", pressure equalized EIF systems as they become available, provided that they meet with the requirements of this Section and do not restrict competition to less than three manufacturers.

CONTROL JOINTS

Detail square edged routed recesses in insulation to receive control joint accessories specified.  Locate as follows:

1.
At corners of windows, doors, louvres and other similarly sized openings.

2.
At changes in substrates.

3.
Spaced at maximum 3.66 m centres.

4.
As required to prevent areas within joints and perimeters exceeding 13.4 m2 and length to width ratio from exceeding 2 1/2 to 1.

INSULATION

All acceptable types of polystyrene insulation should be specified, allowing the Contractor to choose which type to use.  Mineral fibre and glass fibre insulation are typically manufactured with fibres parallel to plane of substrate and exhibit considerably less compressive strength than foamed plastic.  High densities are required to obtain sufficient rigidity to reduce the amount of additional base coat and labour needed to provide an even finished surface.  Fibrous insulations have a relatively large capacity to absorb and store moisture which could seriously affect thermal resistance and deteriorate other components of the system.  For these reasons, glass fibre should not be specified and mineral fibre should be specified only when noncombustibility is a requirement. 

Changes to thermal resistance specified must be supported by data justifying the change and are subject to Alberta Infrastructure approval.  Thicknesses must be adjusted if Alberta natural gas is not the energy source; ensure adjusted thicknesses are readily available.

The requirements of this Section assume substrates are linear.  Curved substrates require curved insulation, or multiple layers of straight insulation.  Verify feasibility with manufacturers, prior to specifying.

TEXTURE AND PATTERN

Pattern and texture are to some extent interchangeable terms when applied to EIFS.  The terminology used here is derived from industry usage.  Texture is determined by the size of aggregate in the finish coat mix.  Aggregate sizes commonly available range from 0.75 mm to 3.0 mm, with 1.5 mm being most common.  

Pattern is determined to a large extent by the ratio of coarse to fine aggregate contained in the finish coat mix.  A mix containing different sized aggregates is commonly used to produce a varied pattern such as for random track finishes.  A mix containing uniform aggregate sizes produces a consistent pattern such as for sand float and random wave finishes.

COLOUR
Do not specify darker colours in combination with expanded polystyrene insulation (EPS), as they may absorb enough solar energy to deform EPS.

END OF DATA SHEETS

1.
General

1.1
SECTION INCLUDES

.1
This Section includes supply and installation of a polymer modified, (Class PM) "hard coat" or "thick coat" exterior insulation and finish system (EIFS) consisting of:

.1
Insulation.

.2
Mesh/insulation fastening devices.

.3
Lamina, made up of base coat, mesh reinforcement, and finish coat.

.4
Joint sealants and other accessories.

1.2
RELATED SECTIONS

.1
Fastener substrates:
Section [04200] [05411] [06100].

.2
Sheet Membrane Air and Vapour Seal:
Section 07261.

.3
Doors:
Section [08411] [    ].

.4
Windows:
Section [08520] [    ].

.5
[     ]:
Section [    ].

1.3
REFERENCE DOCUMENTS

.1
Materials and installation shall meet or exceed requirements in "EIMA Guideline Specification for Exterior Insulation and Finish Systems Class PM", 1991 edition, published by the  EIFS Industry Members Association (EIMA).

.2
Where there is a difference between this specification and the above noted reference document, this specification shall govern.

1.4
PERFORMANCE REQUIREMENTS

.1
System shall meet or exceed performance specified in EIMA Guideline Specification for Exterior Insulation and Finish Systems, Class PM.

.2
Fade Resistance:  no more than slight colour change after accelerated weathering.

1.5
SUBMITTALS

.1
Comply with requirements of Division 1.

.2
Submit system manufacturer's product data, verifying products comply with specified requirements.  Include installation instructions.

.3
Submit evidence that applicator is approved by system manufacturer for the work specified and that installers include technicians trained by system manufacturer.

.4
Submit duplicate 25 mm thick x 300 mm x 300 mm samples of EIFS specified, on 13 mm thick wood panel.  Samples shall include the following:

.1
Finish coat in each colour and texture specified, on primer, base coat, mesh reinforcement and insulation.

.2
A 300 mm bead of sealant in each colour specified, applied as specified to joint in finish coat sample.

.3
At least one fastening device, exposed for inspection.

.4
Successively omit layers to show at least 40 mm width of each component of the layered construction.

.5
Submit system manufacturer's maintenance data [for inclusion in Operation and Maintenance Manual].

.6
Submit written approval by system manufacturer, of products used in the system which are not supplied by the system manufacturer.

SPEC NOTE:  Include following clauses if EIFS is specified to meet regulatory requirements.  Refer to Data Sheet - Code Requirements.

.7
Submit test report verifying proposed system meets regulatory requirements specified in this Section.

1.6
CERTIFICATION

.1
Polystyrene insulation shall be certified for conformance with CGSB 51.20‑M87, Thermal Insulation, Polystyrene, Boards and Pipe Covering, in accordance a certification program accredited by the Standards Council of Canada.

SPEC NOTE:  Include following clause if Regulatory Requirements article is specified.

.2
Promptly upon completion of work of this Section, submit letter certifying that materials and installation are consistent with system verified by test to comply with regulatory requirements specified.

1.7
APPLICATOR QUALIFICATIONS

.1
The EIFS applicator firm shall be approved by system manufacturer.

.2
Installation shall be performed by trained personnel, or a combination of trained and untrained personnel, provided that untrained personnel are always under direct supervision of a trained applicator working as part of the installation crew. 

1.8
REGULATORY REQUIREMENTS

SPEC NOTE:  Include this article when system is required to meet applicable Alberta Building Code requirements for combustible cladding.  Edit to suit project requirements.  Refer also to Data Sheet - Code Requirements.

.1
EIFS shall meet the Alberta Building Code, as follows:

.1
[Subsection 3.1.5. - Noncombustible Construction, Article 3.1.5.5 - Combustible Cladding] [, and]

.2
[Subsection 3.2.3. - Spatial Separation and Exposure Protection of Buildings, Article 3.2.3.7. - Construction of Exposing Building Face, Clause (3)(c)] [, and] 

.3
[Subsection 3.2.3. - Spatial Separation and Exposure Protection of Buildings, Article 3.2.3.7. - Construction of Exposing Building Face, Sentence [(1)] [(2)], requirements for noncombustible cladding].

.2
EIFS specified to comply with the Alberta Building Code shall also meet requirements specified in this Section. 

SPEC NOTE:  Ensure requirements specified in this Section do not conflict with the Alberta Building Code.  Verify currency of Code references.

1.9
MOCK‑UP

SPEC NOTE:  Include this article for projects with complex detailing or unusual methods of fabrication or finishing.

.1
Prior to installation of system, provide minimum 2.4 m x 2.4 m site mock-up showing methods of attachment, terminations at [wall openings and penetrations, reveals, custom shapes, flashings, joints, colours and textures required] [location determined by Minister].

.2
Approved mock-up will establish a minimum standard and may [not] be incorporated into finished work of this Section.  Retain approved mock-up for reference during construction.  Promptly remove rejected mock-ups from site.

1.10
INSPECTION BY MINISTER

SPEC NOTE:  Include this article for large or complex projects, where Alberta Infrastructure has committed to pay for EIFS inspection services.

.1
Minister will appoint and pay for services of an agency to inspect work of this Section.  This inspection is not intended to replace or limit, in any way, Contractor's quality control procedures.

.2
Provide reasonable notice to the Minister to allow for inspection of each stage of the work of this Section.

1.11
DELIVERY, STORAGE AND HANDLING

.1
Deliver products in original, unopened containers and packaging, with manufacturer's labels intact, identifying products, best‑before dates, testing agency compliance and material handling safety information.

.2
Maintain materials in a dry area, protected from weather and temperatures below 5 degrees Celsius.  Do not use materials suspected of having been frozen.

1.12
ENVIRONMENTAL CONDITIONS

.1
Apply materials when relative humidity is less than 50%, and ambient and surface temperatures will be above 5 degrees C during and for a minimum of 24 hours after application.

.2
Protect work from moisture, wind and direct sunlight which could adversely affect the installation.

1.13
COORDINATION AND SEQUENCING

.1
Coordinate work of this Section with the following items penetrating the system, to avoid such penetrations occurring after installation of the EIFS: 

.1
Supports for [light fixtures,] [radiant panels,] [awnings,] [signs,] [flagpoles] [      ] and other attachments.

.2
Plumbing, gas, electrical and other service penetrations.

.3
Other, similar penetrations.

.2
Other items requiring coordination shall include, but shall not be limited to, the following:

.1
Larger openings such as windows, doors, air grilles, access panels and other similar items.

.2
Flashings, trim and joint sealants abutting EIFS but not included in the work of this Section.

2.
Products

2.1
[COMBUSTIBLE] INSULATION

SPEC NOTE:  Include this article if Alberta Building Code permits combustible cladding for this project.  

.1
Expanded Polystyrene:  to CAN/CGSB 51.20‑M87, Type 2, 3 or 4, and as follows:

.1
Type 2 or 3, Moulded Expanded (MEPS):  63.5 mm thick, also meeting EIFS Industry Members Association (EIMA) Guideline Specification for Expanded Polystyrene (EPS) Insulation Board, 1992.

.2
Type 4, Extruded Polystyrene (XEPS):  51 mm thick.

.2
Nominal Maximum Board Size:  600 mm x 1200 mm.

.3
Where requirements of the CGSB standard  and EIMA Guideline Specification differ, the more stringent requirement shall apply.

2.2
NONCOMBUSTIBLE INSULATION

SPEC NOTE:  Include this article only if Regulatory Requirements require noncombustible cladding.  Refer to Data Sheet - Code Requirements.

.1
Mineral Fibre:  meeting acceptance criteria of CAN4-S114-80 and to CAN/CGSB‑51.10‑92, rigid, 63.5 mm thick, minimum RSI 1.76 m2•°C/W, and having minimum density as follows:

.1
Where fibres are parallel to plane of substrate:  128 kg/m3.
.2
Where fibres are perpendicular to plane of substrate:  96 kg/m3.

2.3
FASTENING DEVICES

.1
Provide surface mounted plastic washer specifically designed to secure EIFS, to provide mechanical key for base coat, and as follows:

.1
Washer:  minimum 38 mm diameter with mechanical fastener recess minimum 12.5 mm.

.2
Fastener:  carbon steel with corrosion resistant finish, or stainless steel, suitable for substrate and length to allow minimum 25 mm penetration into substrate.

.2
Corrosion Resistance of Fasteners:  carbon steel fasteners shall show not more than 15% surface rust, and coatings shall not blister, peel or crack, when tested to Corrosion Test Procedure of Factory Mutual Research Approval Standard, Class I Roof Covers (4470).  

.3
Accessory, Joint and Bead Fasteners:  plastic, type to suit insulation and joints and beads, minimum 16 mm diameter head and minimum 25 mm length.

2.4
MESH REINFORCEMENT

.1
Provide open, balanced weave square mesh, minimum 205 g/m2, with continuous glass fibres interlaced in both directions, coated with alkali resistant and abrasion resistant plastic, strand spacing and size as recommended by system manufacturer for PM systems, consistent with minimum weight specified.

2.5
BASE COAT

.1
Base Coat:  system manufacturer's dry or wet mix, consisting of the following, proportioned and mixed strictly to manufacturer's instructions, except as specified otherwise:

.1
Polymer:  acrylic.

.2
Cement:  Type 10 (Normal) Portland, to CAN/CSA-A5-93.

.3
Polymer Content:  minimum 20% by weight of polymer/cement mix.

.4
Fibre Reinforcement:  chopped glass fibre strands.

.5
Water:  clear and potable.

2.6
FINISH COAT

.1
Finish Coat:  factory‑mixed, 100% acrylic emulsion with integral colour and aggregate, proportioned and prepared in strict accordance with manufacturer's instructions, to provide the following appearance characteristics: 

.1
Texture:  [Fine] [Medium] [Coarse] [as indicated in the Finish Coat Schedule at end of this Section].

SPEC NOTE:  Use Finish Coat Schedule at end of this Section when more than one texture, pattern or colour is specified.  Refer to schedule for recommended combinations of texture and pattern.

.2
Pattern:  [sand float] [random track] [random wave] [pebbled] [as indicated in the Finish Coat Schedule at end of this Section].

.3
Aggregate Size:  as required to provide specified texture and pattern, but not greater than 3 mm diameter.

.4
Finish Coat Colour[s]:  selected by Minister from manufacturer's standard range.

SPEC NOTE:  Manufacturers' standard ranges are subject to unanticipated change.  

OR
.4
Finish Coat Colour[s]:  Match [      ]. 

SPEC NOTE:  Consult with manufacturers to determine feasibility of colour matching.  Be as specific as possible when requiring a colour match as there are cost implications.  Specify match to a commercially available paint colour, or specify at least three acceptable EIFS manufacturers' colours by name.

OR
.4
Finish Coat Colours:  as indicated in the Finish Coat Schedule at end of this Section.

2.7
JOINT SEALANTS

.1
Primer:  non‑staining, water-based type, compatible with base and finish coats, and as recommended by sealant manufacturer.

.2
Backer Rod:  round, closed cell foam, extruded polyethylene, urethane or neoprene, Shore A hardness of 20, tensile strength 140 to 200 kPa, oversized 1/3 of joint width, compatible with sealant and primer, non‑adhering to sealant.

.3
Sealant:  silicone base, one or two component, to CAN/CGSB‑19.13‑M87, chemical curing, non-staining, compatible with system substrates, and the following:

.1
Rheological Class: 2 ‑ non‑sag.

.2
Movement Class:  minimum 40.

.3
Temperature Class:  L ‑ low temperature.

.4
Colour:  [to match [finish coat] [      ]].

SPEC NOTE:  Verify sealant colour availability prior to specifying.

2.8
ACCESSORIES

.1
Expansion and Control Joints:  sheet steel to ASTM A653M-96, with Z275 zinc coating designation, flexible joint, expanded metal flanges, deep 'V' profile, sized to suit lamina thickness.

.2
Casing and Corner Beads:  sheet steel with Z275 zinc coating to ASTM A653M‑96, expanded metal flanges, sized to suit lamina thickness.

.3
Flashing:  sheet steel, hot dip galvanized to ASTM A653M-96, Z275 coating [, prepainted to meet or exceed Stelco/Dofasco Series 5000, [colour selected by Minister from manufacturer's standard range] [custom colour to match [     ]]].

.4
Finish Coat Primer:  water-based, as recommended by system manufacturer [, tinted to match finish coat].

SPEC NOTE:  Primer should match finish coat if vandalism or accidental impact is an anticipated risk.

SPEC NOTE:  Delete following two clauses if not applicable.  Adhesive for mineral wool insulation shall be additional to air and vapour seal membrane.

.5
Insulation Adhesive:  as recommended by system manufacturer [for adding rigid insulation shapes and profiles to base rigid insulation layer] [for adhering mineral wool insulation to substrate, compatible with air and vapour seal].

.6
Insulation Shapes and Profiles:  rigid insulation as specified, shaped and profiled as detailed on drawings.

SPEC NOTE:  Verify that drawings detail shapes and profiles.

3.
Execution

3.1
EXAMINATION AND PREPARATION

.1
Protect work of other Sections to prevent soiling from work of this Section, using temporary coverings or other temporary protective measures acceptable to the Minister.
.2
Verify substrate conditions are acceptable prior to installing system components.  Do not start until unsatisfactory conditions have been corrected.

.3
Verify that penetrations through, and items abutting EIFS have been installed and sealed to sheet membrane air and vapour seal.

3.2
INSTALLATION OF INSULATION 

.1
Prior to installing mesh reinforcement, install at least two fastening devices per 600 x 1200 insulation board, at mid-height, to temporarily secure insulation.  These will be additional to fastening devices specified under Mesh Installation.  

.2
Install insulation board horizontally [, starting from a level base line].  Butt boards  tightly. [Size width of starter row to offset board joints 300 mm from sheathing joints.] 

SPEC NOTE:  Specify offsetting board joints if substrate is sheathing.

.3
Install boards in a running bond pattern, offsetting vertical joints minimum 300 mm.  Cut boards as required to locate board joints minimum 200 mm from corners of wall openings and penetrations. 

.4
Provide factory square edges at 90 degree corners.  Alternate overlap of vertical joints at outside and inside corners.  Align exposed edges flush with face of adjoining boards.  

.5
Provide straight, square-edged joints through insulation at substrate expansion joints.  Provide straight square-cut recesses at control joints, accurately sized to suit control joint accessories.  

.6
Tightly fill open board joints with slivers of insulation.  Accurately widen open joints as required so they can be filled with slivers.  Do not fill joints with adhesives or sealants. 

.7
[Cut and shape insulation to conform accurately to special profiles and at locations indicated on drawings.]  

.8
Provide an even and consistent insulation surface, free of dirt, rough spots, raised edges.  Foamed plastic surfaces shall be free of oxidation.

3.3
INSTALLATION OF ACCESSORIES 

.1
Install expansion and control joints before mesh reinforcement, using nylon accessory fasteners.

.2
Locate expansion joints at building expansion joints [and where indicated on drawings].

SPEC NOTE:  Ensure joints are indicated on drawings.

.3
Locate control joints as indicated on drawings.

SPEC NOTE:  Delete following requirements for adhesives and shapes and profiles if not applicable.

.4
Apply adhesives using a notched trowel with maximum 10 mm deep "U" shaped notch.  Provide uniform and horizontal ribbons of adhesive.  

.5
Press insulation material for shapes and profiles into adhesive to ensure maximum adhesion.

.6
Apply minimum 1 mm thick finish coat primer to dry and hard base coat, where finish coat is required.

3.4
MESH INSTALLATION 

.1
Install mesh free from wrinkles, cuts, frayed ends, bulges and other irregularities.  

.2
Install casing, corner beads, expansion joints or starter strips around edges of insulation at EIFS perimeter, wall openings, building expansion joints, and penetrations through EIFS.

.3
Install mesh at reveals, recesses, and over added shapes and profiles.  

.4
Install mesh at external corners turning 30 degrees or more.  

.5
Secure mesh through insulation to structural sheathing, framing, masonry or concrete, using fastening devices located at [300] [400] mm centres [as required to suit framing], and 150 mm from 600 x 1200 insulation board edges.  Washers shall protrude no more than 1 mm above surface of surrounding mesh.  

SPEC NOTE:  Coordinate spacing of fastening devices with spacing of framing, if applicable.

.6
Embed additional 240 mm x 300 mm mesh diagonally at each corner of wall openings into first layer of base coat.  Provide additional minimum 300 mm width mesh around penetrations.

3.5
BASE COAT APPLICATION

.1
Apply base coat in strict accordance with manufacturer's instructions.  

.2
Trowel apply base coat over mesh reinforcement, in thickness adequate to completely embed reinforcing mesh, but not less than 5 mm.

.3
Provide consistent base coat thickness and smooth, even surface, free of rough spots, ridges or other irregularities. 

.4
Provide additional reinforcing mesh as specified during application of base coat.

3.6
FINISH COAT APPLICATION 

.1
Apply finish coat to exposed EIFS surfaces.  Do not apply finish coat on surfaces to receive sealant.

.2
Apply finish coat in accordance with manufacturer's instructions, to provide texture and pattern specified.

.3
Maintain a wet working edge during finish coat application.  Terminate work only at changes in wall direction, control joints and expansion joints.

SPEC NOTE:  Include following clause if two or more types or colours of finish coat are specified.

3.7
JOINT SEALANT APPLICATION

.1
Prepare substrates as recommended by sealant manufacturer.

.2
Examine joint dimensions and select backer rod 30-50% greater than joint width.

.3
Install backer rod to provide joint sealant depth between 1/4 and 1/2 of joint width.

.4
Mask adjacent surfaces with tape prior to priming.

.5
Prime sides of joints to sealant manufacturer's directions prior to caulking.

.6
Apply joint sealant in accordance with manufacturer's directions. 

.7
Form surface of sealant smooth, free of ridges, wrinkles, sags, air pockets, embedded impurities.  Neatly tool surface to a slight concave joint.

.8
Remove excess sealant and droppings immediately, using recommended cleaners approved by EIFS manufacturer, as work progresses.  Remove masking tape after tooling of joints.  Leave work neat and clean.

3.8
CLEANING

.1
Remove excess materials from the site.  Leave surrounding areas free of debris, spills and foreign substances arising from the work of this section.

3.9
FINISH COAT SCHEDULE

SPEC NOTE:  Use this schedule if more than one texture, pattern or colour is specified. 

Location


Texture
Pattern
Colour






[            ]
[Medium]
[Flat, random
[      ]



tracks]




[Sand float]







[            ]
[Fine]
[Random wave]
[      ]



[Sand float]







[            ]
[Coarse]
[Pebbled]
[      ]



[Flat, random




tracks]







[            ]
[      ]
[        ]
[       ]



END OF SECTION
BMS Basic Master Specification


Alberta Infrastructure

Master Specification System
Page 01


