Section Cover Page

Section 07811 1999-09-23 Cementitious Fireproofing

Use this Section to specify spray applied cementitious (rigid and relatively hard) fireproofing for structural steel members such as columns, beams, joists, and metal roof/floor decking assemblies.

Do not specify cellulose fiber, mineral fiber, magnesium oxychloride, or intumescent coating fireproofing materials in this Section.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Related Sections

1.2	Submittals

1.3	Applicator Qualifications

1.4	Mock-Up

1.5	Testing and Inspection By Minister

1.6	Environmental Requirements

2.	Products

2.1	Materials

3.	Execution

3.1	Verification of Conditions

3.2	Protection of Existing Work

3.3	Substrate/Surface Preparation

3.4	Application

3.5	Cleaning

3.6	Fire Resistance Rating Schedule

Applicable Standards

.1	ASTM C847-95	Metal Lath

.2	ASTM E84-96a	Surface Burning Characteristics of Building Materials

.3	ASTM E119-95a	Fire Tests of Building Construction and Materials

.4	ASTM E605-93(1996)	Thickness and Density of Sprayed Fire-Resistive Material (SFRM) Applied to Structural Members

.5	ASTM E736-92	Cohesion/Adhesion of Sprayed Fire-Resistive Materials Applied to Structural Members

.6	ASTM E760-92(1996)	Effect of Impact on Bonding of Sprayed Fire-Resistive Material Applied to Structural Members

.7	ASTM E761-92	Compressive Strength of Sprayed Fire-Resistive Materials Applied to Structural Members

.8	ASTM E859-93	Air Erosion of Sprayed Fire-Resistive Materials (SFRMs) Applied to Structural Members

.9	CAN/ULC-S102-1988	Surface Burning Characteristics of Building Materials and Assemblies

These reference documents may be available for reference purposes in the Technical Resources and Standards Branch Library, Alberta Infrastructure, 3rd Floor, 6950 - 113 Street, Edmonton; Telephone: (780) 427-7924.

1.	General

1.1	RELATED SECTIONS

.1	Plaster Fireproofing:	Section 09211.

.2	Intumescent Coatings:	Section [   ].

1.2	SUBMITTALS

.1	Comply with requirements of Division 1.

.2	Submit, upon request, test reports certifying that fireproofing material:

.1	has been tested and approved for use as part of a fire rated assembly, by a testing agency acceptable to authority having jurisdiction, and

.2	meets or exceeds all other specified performance requirements.

1.3	APPLICATOR QUALIFICATIONS

.1	Applicator shall be licensed or otherwise approved by manufacturer of fireproofing materials.

1.4	MOCK-UP

SPEC NOTE:  Include this article for large projects only.

.1	Apply sample section of [    ] m2 in size to representative substrates on site.

.2	Comply with project requirements as to thickness, density of application, fire rating, and finish texture.

.3	Examine installation within [one] [     ] hour of application to determine variance due to shrinkage, temperature, and humidity.

SPEC NOTE:  Time duration for examination should be determined by anticipated shrinkage, temperature and humidity conditions during drying time.  Refer to manufacturers for technical assistance.

.4	Where shrinkage and cracking are evident, adjust mixture and method of application as necessary.

.5	If accepted, mockup will demonstrate minimum standard for the Work.  Mockup may [not] remain as part of the Work.

1.5	TESTING AND INSPECTION BY MINISTER

.1	The Minister [will] [may] appoint and pay for services of testing agency to verify compliance with specified requirements.

.2	Contractor shall correct deficient work and pay for further inspection and testing required to verify compliance with specified requirements.

1.6	ENVIRONMENTAL REQUIREMENTS

.1	Maintain surrounding air and substrate at minimum temperature of 5°C for at least 24 hours before, during and 24 hours after application of fireproofing materials.

.2	Provide ventilation in areas to receive fireproofing during and 24 hours after application, to dry material.

.3	Maintain non-toxic, unpolluted working area.  Provide temporary enclosure to prevent spray from contaminating air.

2.	Products

2.1	MATERIALS

.1	Cementitious Spray Fireproofing:  Factory mixed, asbestos free, cementitious material with aggregate, non-fibrous, blended for uniform texture, and meeting following performance requirements:

| Requirement | Value | Test Method |
| --- | --- | --- |
| Surface Burning |  | CAN/ULC-S102-1988 |
| Characteristics |  | or |
|  |  | ASTM E84-96a |
| Flame Spread | Max. 10 |  |
| Fuel Contributed | Max. 5 |  |
| Smoke Developed | 0 |  |
| Average Dry Density | Min. 240 kg/m3 | ASTM E605-93 |
| Bond Strength | Min. 10 kPa | ASTM E736-92 |
| Impact Resistance | No cracking, | ASTM E760-92 flaking, or delamination |
| Compressive Strength | Min. 24 kPa | ASTM E761-92 |
| Air Erosion | Max. 0.27 g/m2 over 24 hours delamination | ASTM E859-93 |

.2	Water:  clean and potable.

.3	Expanded Metal Lath:  to ASTM C847-95, galvanized.

3.	Execution

3.1	VERIFICATION OF CONDITIONS

.1	Verify that surfaces are ready to receive work.

.2	Verify that clips, hangers, supports, sleeves, and other items required to penetrate fireproofing are in place.

.3	Verify that ducts, piping, equipment, or other items which would interfere with application of fireproofing are not positioned until fireproofing work is complete.

.4	Verify that voids and cracks in substrate are filled, and projections are removed where fireproofing is exposed to view as a finish material.

.5	Beginning of installation means installer accepts existing surfaces.

3.2	PROTECTION OF EXISTING WORK

.1	Protect adjacent surfaces and equipment from damage by overspray, fallout, and dusting.  Mask adjacent work as required.

.2	Close off and seal ductwork in areas where fireproofing is being applied.

3.3	SUBSTRATE/SURFACE PREPARATION

.1	Clean substrates of dirt, dust, grease, oil, loose material, or other matter which may effect bond of fireproofing.

.2	Remove incompatible materials which affect bond by scraping, brushing, scrubbing, or sandblasting.

.3	[Install metal lath over structural members as indicated on Drawings.]

3.4	APPLICATION

.1	Mix and apply fireproofing materials in accordance with manufacturer's written instructions.

.2	Apply fireproofing in sufficient thickness to achieve specified fire resistance rating[s] and with as many passes as necessary to cover substrate with a monolithic blanket of uniform density and texture.

3.5	CLEANING

.1	Remove excess material, overspray, droppings, and debris.

.2	Remove fireproofing from materials and surfaces not specifically required to be fireproofed.

3.6	FIRE RESISTANCE RATING SCHEDULE

| Location | Components | Rating* |
| --- | --- | --- |
| Roof Assembly] | [Beams, joists and underside of metal deck] | [ ]h |
| [ ] | [ ] | [ ]h |
| [ ] | [ ] | [ ]h |
| [ ] | [ ] | [ ]h |
| [ ] | [ ] | [ ]h |
| [ ] | [ ] | [ ]h |

* Fire resistance rating when tested to ASTM E119-95a.

SPEC NOTE:  Schedule all assemblies and components which require cementitious fireproofing to achieve necessary fire resistance ratings.  Modify schedule contents to suit project requirements.

END OF SECTION