Section Cover Page

Section 08520 2000-06-06 Aluminum Windows

Use this section to specify fixed and operable (except horizontal sliding) aluminum window systems installed vertically between floors and ceilings.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Data Sheet – General

.3	Data Sheet - Window Test Data Summary

.4	Specification Section Text:

1.	General

1.1	Section Includes

1.2	Related Sections

1.3	Reference Documents

1.4	Definitions

1.5	Design Criteria

1.6	Samples

1.7	Shop Drawings

1.8	Test Reports

1.9	Operation and Maintenance Data

1.10	Mock-Up

  - Testing By Minister

2.	Products

2.1	Materials

2.2	Single Unit Fixed Windows

2.3	Single Unit Operable Windows

2.4	[Combination] [and] [Composite] Windows

2.5	Glass and Glazing Accessories

2.6	Hardware

2.7	Exterior Sills

2.8	Interior Sills

2.9	Infill Cladding

2.10	Accessories

2.11	Fabrication

2.12	Anodized Finishes

2.13	Fluoropolymer Paint Finishes

  - Acrylic Paint Finishes

3.	Execution

3.1	Window Installation

3.2	Sill Installation

3.3	Glazing

3.4	Sealant Application

3.5	Adjusting

3.6	Cleaning

3.7	Window Schedule

Applicable Standards:

.1	AAMA 603.8-92	Voluntary Performance Requirements and Test Procedures for Pigmented Organic Coatings on Extruded Aluminum

.2	AAMA 605.2-92	Voluntary Specification for High Performance Organic Coatings on Architectural Extrusions and Panels

.3	ASTM A653M-96	Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot Dip Process

.4	ASTM E283-91	Determining the Rate of Air Leakage Through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen

.5	CAN/CSA-A440-M90	Windows

.6	CAN/CSA-A440.1-M1990	User Selection Guide to CSA Standard CAN/CSA-A440-M90, Windows

.7	CAN/CSA-G40.21-M92	Structural Quality Steels

.8	CAN/CSA-G164-M92	Hot Dip Galvanizing of Irregularly Shaped Articles

These reference documents may be available for reference purposes in the Technical Resources and Standards Branch Library, Alberta Infrastructure, 3rd Floor, 6950 - 113 Street, Edmonton; Telephone:  (780) 427-7924.

REFERENCE STANDARD

This master specification section is based on CAN/CSA-A440-M90, Windows and its appended Special Publication A440.1-M1990, User Selection Guide to CSA Standard CAN/CSA-A440-M90, Windows.  Primarily performance-based, CAN/CSA-A440-M90 also includes prescriptive requirements governing, for example, minimum thickness of aluminum, incorporation of a thermal break, and minimum finish coating thickness for different types of finishes.  There are limitations to this standard, one of them being that its scope is largely limited to single window units, either fixed or operable, but not combination or composite windows.

To properly edit this Section, it is essential that the specifier have a copy of the standard on hand and be familiar with its content.  If you do not have a copy of the standard, contact Alberta Infrastructure Specifications and Standards Section.

TESTING, GENERALLY

Performance of windows installed on buildings is often considerably lower than performance achieved by windows installed in the laboratory.  One common reason is that windows on buildings do not match the window tested.  For example, for test purposes, some manufacturers sealed the insulating glass unit to the window frame with silicone sealant applied all around.  Such installations do not represent typical design or construction practice and provides air and water tightness not normally achieved when installed on site.  Most windows tested used clear glass but others used low E coatings or films and argon gas in sealed units.  It is necessary to have a complete description of windows tested to better understand a manufacturer's test results.

Another reason for lower performance has been found to be faulty installation.  Laboratory installations generally do not exactly duplicate the full range of field conditions windows will be subjected to.

Test methodology may not be representative of actual conditions.  For example, CSA A440 requires thermocouples to be located 50 mm from frame and sash, for condensation resistance testing.  This is considered by some to be too far from bottom of glass lite and to result in overestimating condensation resistance.  As another example, CSA A440 only tests air leakage due to infiltration, not exfiltration.

TESTING BY MINISTER

This Section provides the option of specifying field and laboratory testing.  Exercising this option can result in considerable expense and should therefore be justifiable on the basis of project size and potential consequences of failure.  Obtain Alberta Infrastructure approval in writing prior to specifying such testing by the Minister.

COORDINATING DRAWINGS AND SPECIFICATIONS

Combining performance and prescriptive requirements for windows frequently results in conflicting requirements.  For example, drawings indicate a specific type of frame for which standard sealed units are specified, and the specification calls for a temperature index which testing shows the window cannot provide.

Usually it is desirable to include prescriptive requirements to control appearance and to ensure positive attachment of an air/vapour seal membrane to the window frames.  Verify with manufacturers that window assemblies specified and detailed for the project have been tested and meet performance requirements specified.  Drawings prepared to show appearance and window type as part of the combined prescriptive/performance approach should show the frame profile intended, including critical dimensions, and window design should follow manufacturers' recommendations to achieve the specified performance.

If the performance method of specifying is used, and the appearance of windows and method of glazing is not limited to one type, drawings should show only location, type, and in a schematic way, relationship to adjoining construction.  Do not provide details of frame profiles which may be interpreted to conflict with performance requirements, and vice versa.

DESIGN CONSIDERATIONS

The CSA standard represents a consensus among manufacturers of residential and commercial windows.  Manufacturers of the latter are capable of substantially exceeding CSA A440 air tightness ratings (infiltration only).  Pressures causing exfiltration at building corners can exceed those causing infiltration.  Coordinate specifying Temperature Index with current issue of Alberta Infrastructure "Design Requirements for Buildings".

Review assumptions behind CSA A440 ratings to determine if performance requirements need to be upgraded for more severe conditions.  It is possible to specify higher performance than CSA ratings and to specify additional performance requirements not included in the standard.  Doing so, however, must be justifiable on the basis of functional requirements and life-cycle cost criteria.  This is particularly so if specifying more stringent performance requirements will result in only one or two manufacturers being capable of meeting the specification.

The following is based on information provided by window manufacturers, as of May, 1993.  It is intended to inform the specifier of the approximate capability of manufacturers to meet or exceed CSA A440.  Refer to Data Sheet article titled "Testing, Generally" for some considerations regarding testing.  Window specimens tested are not necessarily representative of industry practice.  DBL test data required for temperature index.

| Aluminum Window Description |  | Air Tightness (m3/h)m-1 | Water Tightness | Wind Resist- ance | Temperature Index |
| --- | --- | --- | --- | --- | --- |
| Fixed, Exterior Glazed |  |  |  |  |  |
|  | Kawneer 1600 (box frame profile) | 0.46x10-4 (m3/s/m2*) | B7 | C4 | 61** |
|  | Kawneer KAW-F1 (box frame profile) | 0.030 | B7 | C5 | Ig = 76.6** |
|  | Prevost 3800 (box frame profile) | 0.184 | B7 | C5 | Ig = 56.0** |
| Fixed, Interior Glazed, Snap-on Stops |  |  |  |  |  |
|  | Kawneer 516 | 0.020 | B3 | C3 | If = 57.6 |
|  | Kawneer 517 | 0.094 | B3 | C3 | If = 60.3 |
|  | Kawneer 518 | 0.020 | B3 | C3 | If = 58.1 |
|  | Alumicor Model 230 | 0.01 | B7 | C5 | Ig = 64 |
|  | Lorlea 560, 564, 590, 594 | 0.05 | B3 | C3 | 55 |
|  | DBL Series 900 | "not measurable" | B3 | C3 | 69.3 |
|  | DBL Series 1100 | "not measurable" | B3 | C3 | 71.6 |
|  | Prevost 20-350 (tested to A440-M84) | 0.0172 | B3 | C1 | D2 |

* Based on window area, not crack length.

** Depends on depth of frame used.

| Aluminum Window Description |  | Air Tightness (m3/h)m-1 | Water Tightness |  | Wind Resist- ance |  | Temperature Index |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Fixed, Interior Glazed, Snap-on Stops (Continued) |  |  |  |  |  |  |  |
|  | Prevost 80-400 (tested to CSA A440-M90) | 0.024 | B3 |  | C1 |  | D2 |
|  | Visionwall Series 100 | 0.063 | B7 |  | C5 |  | Ig = 73 |
| Fixed, Other types |  |  |  |  |  |  |  |
|  | DBL Series 100 (Site Seal) | 0.11 | B3 |  | C3 |  | 62.9 |
| Casements |  |  |  |  |  |  |  |
|  | Kawneer 526 | A3 | B7 |  | C5 |  | 56 |
|  | DBL Series 800 | 0.16 | B2 |  | C3 |  | 68.8 |
|  | Visionwall Series 100 | 0.058 | B7 |  | C5 |  | Ig = 73 |
| Awning Type |  |  |  |  |  |  |  |
|  | Kawneer 526 | A3 | B7 |  | C5 |  | 56 |
|  | DBL Series 700 | A3 | B3 |  | C3 |  | 71.1 |
|  | DBL Series 1300 | A3 | B7 |  | C5 |  | 68.4 |
| Hopper Type |  |  |  |  |  |  |  |
|  | Kawneer 526 | A3 | B7 |  | C5 |  | 56 |
|  | Alumicor 210 Series | 0.10 | B7 |  | C5 |  | If = 56.3 |
|  | DBL Series 600 | 0.43 | B2 |  | C3 |  | If = 70.5 |
|  | Lorlea 540 Series (tested to CSA A440-M90) | 0.43 | B2 |  | C3 |  | If = 70.5 |
|  | Prevost 1700 | 0.234 | B7 |  | C5 |  |  |
|  | Prevost 1800 | 0.056 | B7 |  | C5 |  | Ig = 56.4 |
| Tilt & Turn type |  |  |  |  |  |  |  |
|  | Prevost 1950 | A3 | B7 |  | C4 |  | If = 48 |

END OF DATA SHEETS

1.	General

1.1	SECTION INCLUDES

.1	This Section specifies aluminum window systems, of the following type[s], installed in exterior walls:

.1	Single [fixed] [operable] units.

.2	Composite with [fixed lites only] [operable lites only] [fixed and operable lites].

.3	Combination with [fixed lites only] [operable lites only] [fixed and operable lites].

.2	Some components of aluminum window systems are specified in related sections.

1.2	RELATED SECTIONS

SPEC NOTE:  For projects of significant size or complexity and requiring special attention to building envelope performance, consider specifying mock-up of representative wall system in modified Section 01450 - Quality Control, or creating new Section 01434 - Mock-ups.

.1	Mock-up including work of this Section:	Division 1.

.2	Sheet Membrane Air and Vapour Seal	Section 07261.

.3	Sealants:	Section 07920.

.4	Glass and Glazing General Requirements:	Section 08801.

1.3	REFERENCE DOCUMENTS

.1	Materials, fabrication, attachments, accessories, assembly and performance shall meet or exceed requirements of CAN/CSA-A440-M90.

1.4	DEFINITIONS

SPEC NOTE:  Include applicable definitions only.

.1	Single Unit Window:  a window consisting of one fixed or one operable lite.

.2	Composite Window:  a window consisting of two or more lites in one main frame.  Composite windows may consist of fixed or operable windows, or a combination of both.

.3	Combination Window:  a combination of two or more complete window assemblies whose frames are mulled together.  Combination windows may consist of fixed or operable windows, or a combination of both.

1.5	DESIGN CRITERIA

SPEC NOTE:  Include following clause if drawings do not indicate frame design intent for all types of windows.

.1	Fixed glazing specified in this Section shall be installed from the [exterior] [interior] [, except as indicated otherwise on drawings].

OR

SPEC NOTE:  Include following clause if drawings indicate frame and sash profile design intent.  Ensure frame design detailed does not conflict with performance requirements.

.1	Frame and sash profiles detailed on drawings indicate basic design intent.

.2	Provide products designed to meet specified performance requirements.

.3	Design frames to equalize pressure between outside air and:

.1	cavities surrounding glass units, and

.2	cavities surrounding operable sash.

.4	Provide drainage from all spaces around insulating glass units, including each horizontal space created by setting blocks.

.5	Provide baffles or other protection at drainage openings to prevent direct entrance of wind-driven rain.

.6	Provide frames and sash designed to provide mechanical key for glazing splines and gaskets.

SPEC NOTE:  Establish wind load based on Climatic Data included in Alberta Building Code and modified by factors based on engineering analysis.

.7	Provide window anchorage to withstand [    ] Pa wind load and to distribute wind load along frames to window manufacturer's recommendations.

.8	Design components to accommodate thermally induced movement.

1.6	SAMPLES

SPEC NOTE:  Consider scope of this Section, complexity of design, and importance of appearance before specifying any or all samples.

.1	Comply with requirements of Division 1.

.2	Submit duplicate 200 mm x 200 mm sample of fabrication of the following:

.1	Window frame corners at sills.

.2	Typical anchoring devices and connection to frame.

.3	Mullion intersecting head and sill frame.

.4	[Operable sash installed in typical frame.]

.5	[Insect screens, in sash.]

.6	Non-standard conditions.

.3	Submit five 100 mm long samples of anodized aluminum to indicate maximum range of anodized colour variation for project.

.4	Submit duplicate samples of aluminum finished to indicate colour, gloss and type of paint finishes specified.

.5	[Submit samples of latching devices and exposed hardware to indicate style and finish.]

1.7	SHOP DRAWINGS

.1	Comply with requirements of Division 1.

.2	Submit detailed and complete description of differences between windows tested for conformance to this specification, and windows intended for this project.  Include elevations and full scale details to show physical differences.

.3	Provide elevation views.  Indicate components, materials, finishes, and locations of anchorage.

.4	Clearly indicate, in large scale, the following:

.1	Sections details showing all window perimeter conditions.

.2	Mullion [and muntin] details and frame corner connections.

.3	Sill flashing terminations, in isometric view, including coordination with wall cladding materials.

.4	Frame anchorage details.

.5	Details showing sealing techniques within and around perimeter of framing and operable sash.

.6	Connection to building sheet membrane air and vapour seal.

.7	Required sizes and tolerances of openings.

1.8	TEST REPORTS

.1	Comply with requirements of Division 1.

.2	Submit test reports from an independent testing agency acceptable to the Minister, indicating windows to be supplied for project meet specified requirements.

.3	Include complete description of windows tested.

1.9	OPERATION AND MAINTENANCE DATA

.1	Comply with requirements of Division 1.

.2	Submit the following:

.1	Window type and location.

.2	Names of products under each window type, including manufacturer's name and identification of framing components, components of sealed units, weather-stripping, glazing materials, and sealants.

.3	Submit as-built drawings, using reviewed shop drawings, modified to as-built condition.

.4	Submit maintenance instructions for glass and aluminum finishes.

1.10	MOCK-UP

.1	After approval of shop drawings and samples, construct one full size window unit complete with glass and hardware.

.2	Install mock-up window unit in building window opening, complete with flashing and sealed to building air and vapour seal.  Obtain approval of mock-up prior to installation of the work of this Section.

1.11	TESTING BY MINISTER

SPEC NOTE:  Include this article only if there is a stated intent by Alberta Infrastructure to test.  Ensure that performance requirements for the window types to be tested are specified.

.1	Minister will appoint and pay for the services of an independent testing agency to inspect and test [a] window[s].

.2	Window[s] to be tested will be taken at random from manufacturer's fabricating facility.  Notify Minister when window fabrication is completed.

.3	Tests for condensation resistance will be performed on each separate lite of combination and composite windows.  The lowest temperature index calculated will apply.

2.	Products

2.1	MATERIALS

.1	Aluminum:  Aluminum Association (AA) alloy 6063-T5 or 6063-T6 for extrusions and AA 1100, anodizing quality, for sheet.

.2	Steel:  to CAN/CSA-G40.21-M92, hot dip galvanized to CAN/CSA-G164-M92.

.3	Sheet Steel:  to ASTM A653M-96, hot dip galvanized to Z275 coating designation.

SPEC NOTE:  Refer to Data Sheets before specifying performance ratings in the following articles.

2.2	SINGLE UNIT FIXED WINDOWS

.1	Windows shall meet or exceed requirements of CAN/CSA-A440-M90, and the following performance ratings:

.1	Air Tightness:  [Fixed] [maximum [  ] (m3/h)m-1 to ASTM E283-91].

.2	Water Tightness:  [B3] [B5] [B7].

.3	Wind Load Resistance:  [C3] [C5].

.4	Minimum Temperature Index:  [56] [  ].

2.3	SINGLE UNIT OPERABLE WINDOWS

.1	Windows shall meet or exceed requirements of CAN/CSA-A440-M90, and the following performance ratings:

.1	Air Tightness:  [A3] [A[ ]] [maximum [  ] (m3/h)m-1 to ASTM E283-91].

.2	Water Tightness:  [B3] [B5] [B7].

.3	Wind Load Resistance:  [C3] [C5].

.4	Minimum Temperature Index:  [56] [  ].

SPEC NOTE:  CSA A440 allows 5.0 mm for maximum deflection for casement windows.  Include following clause only if a more stringent requirement needs to be specified.

.5	Sash Strength and Stiffness of Casement Windows:  maximum deflection of [  ] mm.

SPEC NOTE:  CSA A440 allows 18.0 mm for maximum deflection of projecting windows.  Include following clause only if a more stringent requirement needs to be specified.

.6	Sash Strength and Stiffness of Projecting Windows:  maximum deflection of [  ] mm.

SPEC NOTE:  The test for resistance to forced entry applies only to operable windows and is not intended to provide more than a basic residential standard of security.

.7	[Pass test for resistance to forced entry.]

SPEC NOTE:  Delete the following clause if not applicable.  Normally specify standard screen strength.

.8	Screens:  aluminum mesh with extruded aluminum sash and four retainers per side, [standard] [heavy duty].  Mesh and sash finishing material shall match window frame.

2.4	[COMBINATION] [AND] [COMPOSITE] WINDOWS

SPEC NOTE:  Delete this article if not applicable.

.1	Meet or exceed requirements of CAN/CSA-A440-M90 for combination and composite windows.

.2	Unless specified otherwise, performance requirements for fixed and operable portions of [combination] [and] [composite] windows shall meet or exceed requirements specified for separate fixed and operable single window units respectively.

.3	Air tightness of crack length along frames mulled together and where lites within one main frame join, shall meet or exceed requirement for fixed windows.

2.5	GLASS AND GLAZING ACCESSORIES

.1	Provide glass for aluminum windows as scheduled in Glass Schedule at end of this Section, and as specified in Section 08801.

.2	Provide glazing materials designed to maintain adequate pressure against glass through full design temperature range experienced through warranty period, regardless of installation temperatures.

.3	Setting Blocks:  neoprene, 80 durometer hardness, 100 mm long x width equal to thickness of supported glass unit x 6 mm high.

.4	Spacer Shims:  neoprene, 80 durometer hardness, 75 mm long x minimum 6 mm thick. Do not use lead, plastic, or wood shims.

.5	Glazing Splines and Gaskets:  manufacturer's standard dry glazing splines and gaskets profiled for glazing stops and glazing retaining devices.  Profiles shall mechanically key into glazing retaining devices. Except where otherwise specified, colour shall match frame colour.

2.6	HARDWARE

SPEC NOTE:  Delete this article if no operable lights on project.  Edit to suit project requirements.

.1	Provide manufacturer's standard hardware in type specified for operable sash [, in finish to match window frame] [           ].

.2	Equip operable windows with hardware as follows:

.1	Top Hung, Opening Out:  [Anderberg friction arms and underscreen stay bar assembly] [hinges and roto operator with locking handle].

.2	Bottom hung, Opening In:  Anderberg friction arms and spring loaded locking device to automatically lock window in closed position.

.3	Casement Type, Opening Out:  stainless steel or extruded aluminum butt hinges, claw handles, roto operator.

.4	Casement Type, Opening In:  stainless steel or extruded aluminum butt hinges, manufacturer's standard.

.3	[Provide [keyed opening devices] [           ] for windows normally locked.]

SPEC NOTE:  Consult with hardware consultants regarding special locking devices and specify in detail.  Indicate locations in a window schedule.

SPEC NOTE:  For sills and cladding, normally specify maximum 1.3 mm thickness for brake formed flashing.  Greater thicknesses result in fissures at tight bends, that are visible at 3 m.  Anodizing after forming is costly for projects involving small quantities of brake formed sheet aluminum.

2.7	EXTERIOR SILLS

.1	Material:  [extruded aluminum] [brake formed aluminum sheet].

SPEC NOTE:  Verify that extruded aluminum sill size and profile are readily available.

.2	Shape and Size:  as detailed on drawings, with minimum 2% drainage slope to exterior unless detailed otherwise on drawings.

.3	Thickness:  minimum [1.3] [2.1] [3.2] [  ] mm thick.

.4	Accessories:  [joint covers, jamb drip deflectors, chairs, anchors] [anchoring devices].

.5	Finish:  same as adjacent window frame] [                 ].

2.8	INTERIOR SILLS

.1	Material:  [extruded aluminum] [brake formed aluminum sheet].

.2	Type and Size:  as detailed on drawings.

.3	Thickness:  minimum [3] [1.6] [  ] mm.

.4	Accessories:  [joint covers] [anchoring devices].

.5	Finish:  [same as adjacent window frame] [                 ].

2.9	INFILL CLADDING

.1	Material:  [extruded aluminum] [brake formed aluminum sheet].

.2	Type and Size:  as detailed on drawings.

.3	Thickness:  minimum [3] [1.6] [  ] mm.

.4	Finish:  [same as adjacent window frame] [                 ].

2.10	ACCESSORIES

.1	Steel Clips, Supports and Reinforcement:  minimum 2.0 mm bare sheet thickness, hot-dip galvanized to CAN/CSA-G164-M92.  Provide anchors that permit sufficient adjustment for accurate alignment.

.2	Joint Sealants:  as specified in Section 07920.

.3	Flexible Joint Membrane:  membrane as specified in Section 07261 - Sheet Membrane Air and Vapour Seal.

2.11	FABRICATION

.1	Fabricate window units square and true with maximum tolerance of plus or minus 1.5 mm for units with a diagonal measurement of 1800 mm or less and 3 mm for units with a diagonal measurement over 1800 mm.

.2	Seal framing joints with butyl-polyisobutylene or silicone sealant.

.3	Arrange components to prevent abrupt variation in colour.

SPEC NOTE:  Normally include following clause for curtain wall box type frame profiles.

.4	Provide glazing retaining devices secured with threaded fasteners.

SPEC NOTE:  Include the following clause if sheet aluminum specified exceeds 1.3 mm in thickness.

.5	[Fabricate and form sheet aluminum prior to colour anodizing or painting.]

SPEC NOTE:  If more than one type of finish or colour are required, ensure locations are indicated on drawings or schedules.

2.12	ANODIZED FINISHES

.1	Provide surface preparation and anodized finish on exposed aluminum surfaces to Aluminum Association Architectural designation, with even distribution of approved colour variation, as follows:

.1	[Clear Anodized Coating:  [to AA M12C22A31, 10-18 micrometre thick, Architectural Class II designation] [to AA M12C22A41, not less than 18 micrometre thick, Architectural Class I designation,].

SPEC NOTE:  Specify AA M12C22A41 coating for typical exterior applications.  Specify AA M12C22A31 coating for interior applications not subject to abnormal wear.

.2	[Colour Anodized Coating:  to AA M12C22A42 or AA M12C22A44, not less than 18 micrometre thick, Architectural Class I designation, [light bronze] [medium bronze] [dark bronze] [black] [      ] colour].

SPEC NOTE:  Consult with manufacturers if other preparation methods or anodized finishes are required, and to verify availability of colours specified.

2.13	FLUOROPOLYMER PAINT FINISHES

SPEC NOTE:  Fluoropolymer coating is the higher performance paint finish.  Some systems may exceed cost of colour anodizing.  Identify coating system and colour as there can be significant cost differences.  Consult with qualified coating applicators.

.1	Provide fluoropolymer paint finish meeting or exceeding test requirements of American Architectural Manufacturers Association specification AAMA 605.2-92 - Voluntary Specifications for High Performance Organic Coatings on Architectural Extrusions and Panels.

.2	Factory apply paint finish on exposed aluminum surfaces, by an applicator qualified by paint manufacturer.  Prepare surfaces in strict compliance with paint manufacturer's recommendations.

.3	Provide paint system consisting of [2] [3] [4] coats, as follows:

.1	First Coat:  primer.

.2	Second Coat:  barrier coat.

.3	Third Coat:  colour coat.

.4	Fourth Coat:  clear protective coat.

.5	Total Dry Film Thickness:    minimum [30.5] [40.6] [  ] micrometer.

.6	Sheen:    medium gloss.

.7	Colour:    match [Duranar [    ]] [     ].

SPEC NOTE:  As a minimum, specify primer and colour coat.  For some coating systems, a barrier coat and/or a clear protective coating is recommended by manufacturers.  Specify 2 coats for 30.5 micrometer thickness and 3 coats for 40.6 micrometer thickness.

2.14	ACRYLIC PAINT FINISHES

SPEC NOTE:  Specify thermosetting acrylic enamel for residential and light duty, low rise institutional applications where cost is primary and the performance of anodized finishes and fluoropolymer coatings is not required.

.1	Provide thermosetting acrylic paint finish meeting or exceeding test requirements of CAN/CSA-A440-M90 or American Architectural Manufacturers Association specification AAMA 603.8-92 - Voluntary Performance Requirements and Test Procedures for Pigmented Organic Coatings on Extruded Aluminum.  Colour shall match Duracron [     ].

3.	Execution

3.1	WINDOW INSTALLATION

.1	Erect and secure window units in prepared openings, plumb and square, free from warp, twist or superimposed loads.

.2	Secure work accurately to structure and in a manner not restricting thermal movement of materials.

.3	Provide shims under sill frame at setting block locations, and as recommended by window frame manufacturer.

.4	Conceal all anchors and fitments.  Exposed heads of fasteners not permitted.

SPEC NOTE:  Specify the following clause when mechanical fastening intent is detailed on drawings.

.5	Mechanically fasten flexible membrane air and vapour seal to window frame with continuous aluminum channel as detailed on drawings.

.6	Maintain dimensional tolerances after installation.  Maintain alignment with adjacent work.

.7	Isolate aluminum surfaces from cementitious materials adjacent after installation, using coating of bituminous paint.

.8	Seal framing joints with butyl-polyisobutylene or silicone sealant.

3.2	SILL INSTALLATION

.1	Set exterior sills with uniform design drainage slope to exterior, level in length.  Extend sills past jambs.

.2	Secure sills in place with anchoring devices located at ends [and joints] and evenly spaced at maximum [600] [   ] mm between.

.3	Provide one piece sill flashing where practicable.  Where joints are required, locate to provide equal sill lengths and provide backup flashing at joints as detailed.  Do not caulk joints.

.4	Provide adequate space between butt ends of sill lengths to allow for thermal expansion.  For sills over 1200 mm in length, maintain 3 to 5 mm expansion space at each end.

3.3	GLAZING

.1	Refer to Section 08801 - Glass and Glazing for general requirements for glazing.

.2	Install glazing splines and gaskets uniformly, with accurately formed corners and bevels.  Ensure that proper contact is made with glass and rabbet interfaces.

.3	Continuously and uniformly compress glazing splines and gaskets 38-50 mm per 1200 mm during installation.

3.4	SEALANT APPLICATION

.1	Install sealant and related materials in accordance with Section 07920 and as detailed on drawings.

3.5	ADJUSTING

SPEC NOTE:  Delete this article if all windows are fixed.

.1	Adjust ventilators and hardware to operate smoothly.  Lubricate moving parts.  Lock settings after alignment.

3.6	CLEANING

.1	Wash down exposed interior metal surfaces using a solution of mild domestic detergent in warm water, applied with soft clean wiping cloths.

.2	Clean exposed exterior non-metal surfaces as recommended by manufacturer of the material.

.3	Clean interior and exterior surfaces as soon as adjacent construction which might soil surfaces, is completed.

3.7	WINDOW SCHEDULE

SPEC NOTE:  Edit schedule to suit window types, including composite and combination.  Coordinate glass type with Section 08801.

| [Window location/ drawing symbol] | Window Type | Finish/Colour | Insulating Glass* |
| --- | --- | --- | --- |
| [All exterior aluminum windows] [ ]/[W1][ ] | [Fixed] [ ] | [Anodized]/[ ] [ ]/[ ] | [IG1] [ ] |
| [ ] | [Top hung, projecting out] | [ ]/[ ] | [ ] |
| [ ] | [Bottom hung, projecting in] | [ ]/[ ] | [ ] |
| [ ] | [Casement, opening out] | [ ]/[ ] | [ ] |
| [ ] | [Casement, opening in] | [ ]/[ ] | [ ] |
| [ ] | [Vertical, sliding] | [ ]/[ ] | [ ] |
| [ ] | [Horizontal sliding] | [ ]/[ ] | [ ] |
| [ ] | [Tilt-turn] | [ ]/[ ] | [ ] |

*Specified in Section 08801.

# END OF SECTION