Section Cover Page

Section 14 01 30 2006-05-01 Escalator Task and Frequency Schedule

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

- Related Sections

- Frequency and Tasks

  - Every Scheduled Visit

  - Monthly

  - Quarterly

  - Semi-Annually

  - Annually

- Related Sections

.1	Elevator Device Maintenance:	Section 14 01 01.

.2	Preventive Maintenance Log Sheet for Escalators	Section 14 01 31.

- Frequency and Tasks

.1	Every Scheduled Visit:

.1	Meet with Minister’s representative, identify and correct all concerns.

.2	Perform all work required to maintain equipment in safe and reliable operating condition, including but not limited to scheduled tasks.

.3	Complete the Minister’s 52-week Work Schedule System Log Sheets and record required information in Log Book.

.2	Monthly:

.1	Remove pit covers/landing plates and inspect, clean, maintain an lubricate as necessary all parts of the machinery including but not limited to:

.1	step chains and rollers

.2	step rollers

.3	top and bottom pit areas

.4	machine brake

.5	automatic chain oilers

.2	Check general operation, clean components as required.

.3	Inspect step skirts for wear of skirting and low-friction coatings, protrusions or gaps. Adjust or repair as required.

.4	Inspect step treads, balustrades, decking, landing plates and combplates for damage, gaps or uneven surfaces. Repair as required..

.5	Inspect handrails for damage, pinching hazards, proper traction, high operating temperature and speed. Adjust or repair as required.

.6	Test emergency stop buttons and start-up key switches for proper operation.

.3	Quarterly:

.1	Inspect and test all safety string devices including but not limited to;

.1	skirt switches

.2	combplate switches

.3	handrail inlet devices

.4	missing step devices

.5	carriage tension devices

.2	Inspect and maintain handrail speed and handrail chain tension.

.3	Inspect, clean and maintain handrail newels and rollers.

.4	Inspect, maintain and adjust the handrail drive mechanism including drive sheaves, drive newels, drive belts and drive chains.

.5	Inspect and maintain proper skirt clearance on side of step.

.6	Inspect and maintain combplates.

.7	Apply friction reducing agent to skirt panels where required.

.8	Inspect and maintain step treads and risers.

.9	Remove at least one step and perform a detailed inspection of the interior truss space including step tracks and all other machinery, Clean and maintain as required.

.10	Inspect demarcation lights.

.11	Check for required caution signs.

.12	Test broken step chain actuating device, maintain chain tension.

.13	Test broken drive chain actuating device, maintain chain tension.

.14	Test step obstruction device.

.15	Inspect speed governor, test speed governor switch.

.16	Inspect machinery space stop switch.

.17	Inspect anti-reversal mechanism.

.18	Inspect step upthrust devices.

.19	Test brakes.

.20	Inspect and maintain clearance between successive steps.

.21	Clean inside face of handrail.  Wax handrail guide if required.  Replace handrail as required.

.4	Semi-Annually:

.1	Grease main drive shaft and bull gear bearings and maintain seals.

.5	Annually:

.1	Clean and adjust step chain novatex curves.  Note excessive or uneven wear.

.2	Remove dirt deposits from step band.  Check for loose track fastening, tighten as required.

.3	Check operation of controller.  Clean and adjust as required.

.4	Check step coast when braking empty unit.

.5	Lubricate step flanges.

.6 	Thoroughly clean the interior truss and pit areas including interior sides of steps, tracks, trusses and machines.

.7	Clean oil drip pans full length of escalator.

.8	Grease handrail sheave bearings at lower and upper reversing stations.

.9	Grease step chain sprockets.

.10	Change oil in gearbox.

.11	Lubricate motor bearings.

.12	Inspect, monitor and repair or replace cracked step frames in accordance with manufacturer’s and industry standards. Number all steps and maintain a detailed logbook record of all steps as and when they are inspected, repaired or replaced.

END OF SECTION