Section Cover Page

Section 15711 Mechanical Draft Cooling 2005-02-08 Towers Inspection and Maintenance

Use this Section to specify maintenance service requirements for mechanical draft cooling towers only.

This Master Specification Section contains:

.1	This Cover Sheet.

.2	Specification Section Text:

1.	General

1.1	Intent

1.2	Related Requirements

2.	Products

2.1	Materials

3.	Execution

3.1	Maintenance Procedures

.3	Section 15711A - Mechanical Draft Cooling Towers Inspection Report

Editing:  Use this Section as is; do not modify in any way.

1.	General

1.1	INTENT

.1	This Section specifies inspection and maintenance requirements for mechanical draft cooling towers and related equipment only.

1.2	RELATED REQUIREMENTS

.1	Refrigeration and Air Conditioning Systems Inspection

and Maintenance General Requirements:	Section 15651

2.	Products

2.1	MATERIALS

.1	Contractors shall provide all necessary lubricants and cleaning materials as required.

3.	Execution

3.1	MAINTENANCE PROCEDURE

.1	Seasonal Start-Up:

.1	Check and remove debris from screens, fans, eliminators, heat transfer sections, and sump.

.2	Flush and clean sump.

.3	Inspect protective finish.

.4	Inspect and clean sump strainers.

.5	Ensure free movement of fan, check belt condition and tension, adjust and/or replace as required.

.6	Lubricate shaft and motor bearings, ensure all set screws and locking collars are tight.

.7	Inspect and clean spray nozzles and heat transfer section.

.8	Check and adjust make-up valve.

.9	Check and adjust bleed rate.

.10	Check pump operation, lubricate as required.

.11	Check and record voltage and current draw of pump and fan motors.

.12	Report any recommendations or deficiencies on Section 15711A

.2	Mid-Season Inspection(s):

.1	Check and remove debris from fans and inlet screens.

.2	Check and clean sump if required.

.3	Inspect and clean sump strainers if required.

.4	Check belt condition and tension adjust and/or replace as required.

.5	Check shaft and motor bearings, lubricate as required.

.6	Inspect and clean spray nozzles as required.

.7	Check and adjust make-up valve.

.8	Check and adjust bleed rate.

.9	Report any recommendations or deficiencies on Section 15711A.

.3	Seasonal Shut-Down:

.1	Ensure any parts of system subject to freezing are properly drained.

.2	Inspect system noting any deficiencies to be corrected, prior to next operating season.

.3	Report any recommendations or deficiencies on Section 15711A.

END OF SECTION